## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.05.16 04:12:28.143 | DMA_TEP_0303_04_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.05.15 20:49:15.463 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.15 20:47:08.471 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.15 19:26:38.810 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.15 19:26:25.767 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.15 19:25:21.767 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.15 19:25:21.767 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.15 10:56:53.983 | PKV-E-PSD-027 | Parkville Platform 2 Zone 3 PSD 27 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.15 10:56:53.983 | PKV-W-PSD-004 | Parkville Platform 1 Zone 1 PSD 04 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.13 17:25:33.943 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK High | 2024.05.13 17:25:33.785 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK High | 2024.05.13 17:25:33.702 | _Driver1_2 | MTAZC:_Driver1_2. | Driver overloaded |  |  |  | 0 | ARN | Servers Comms
CAME UNACK High | 2024.05.13 16:55:24.141 | AEN-E-PED-001 | Arden Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.05.13 16:52:06.138 | AEN-W-PED-002 | Arden Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.05.13 11:47:38.309 | TNC-E-PED-002 | State Library Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.13 11:26:12.610 | TSC-W-PED-002 | Town Hall Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.13 11:11:26.612 | TSC-E-PED-001 | Town Hall Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.13 10:00:38.819 | SKP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.12 21:24:20.318 | PKV-W-PED-002 | Parkville Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.12 21:13:44.329 | PKV-E-PED-001 | Parkville Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.12 19:58:24.614 | TSC-E-PED-002 | Town Hall Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.12 19:50:16.330 | TNC-E-PED-001 | State Library Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.11 19:15:22.819 | SYP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.10 08:49:20.968 | _Driver2_2 | MTTHL:_Driver2_2. | Driver overloaded |  |  |  | 0 | AZC | Servers Comms
CAME UNACK High | 2024.05.09 08:52:02.821 | SYP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.09 04:27:28.821 | SYP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.09 00:18:57.827 | SKP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.08 09:24:26.938 | _Driver1_2 | MTARD:_Driver1_2. | Driver overloaded |  |  |  | 0 | PKV | Servers Comms
CAME UNACK High | 2024.05.07 20:55:46.316 | PKV-W-PED-001 | Parkville Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.07 20:55:32.309 | PKV-E-PED-002 | Parkville Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.07 19:19:16.312 | TNC-W-PED-001 | State Library Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.07 19:13:18.333 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.07 19:01:04.576 | TSC-W-PED-001 | Town Hall Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.07 14:13:49.974 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.06 13:49:44.822 | SYP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 13:21:29.819 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 09:24:49.474 | TSC-W-PSD-030 | Town Hall Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.06 09:24:37.553 | TSC-W-PSD-010 | Town Hall Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.06 09:12:45.472 | SKP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 09:07:20.816 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.901 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.893 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.885 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.877 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.740 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.148 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK Med | 2024.05.16 07:12:38.147 | DMA_FCU_0107_08_FG | Fan Coil Unit - Function Group | Cooling unavailable! |  |  |  | 0 | AZC | Check if recurrent
CAME UNACK Med | 2024.05.15 20:49:15.463 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.15 19:26:38.810 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.15 10:56:53.952 | PKV-S-STN | Parkville Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | PKV
CAME UNACK Med | 2024.05.13 17:47:16.381 | _Mod_Plc_1 | Anzac Server 1 | Communications Fault - Anzac Server 1 to Anzac PSD |  |  |  | 0 | AZC
CAME UNACK Med | 2024.05.11 17:49:31.321 | _Mod_Plc_4_2 | MTPKV:_Mod_Plc_4_2. | ommunications Fault - Parkville Server 2 to Parkville EWIS |  |  |  | 0 | STL | Servers Comms
CAME UNACK Med | 2024.05.10 09:02:15.294 | _Conn_dist_1_2_to_dist_5_2 | Distributed Server 2 | Connection lost to State Library Server 2 - Link 0 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 09:02:15.294 | _Conn_dist_1_2_to_dist_5_2 | Distributed Server 2 | Connection lost to State Library Server 2 - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 09:02:15.294 | _Conn_dist_1_2_to_dist_6_1 | Distributed Server 2 | Connection lost to Town Hall Server 1 - Link 0 |  |  |  | 0 | ARN | Servers Comms
CAME UNACK Med | 2024.05.10 09:02:15.294 | _Conn_dist_1_2_to_dist_6_1 | Distributed Server 2 | Connection lost to Town Hall Server 1 - Link 1 |  |  |  | 0 | ARN | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:20.226 | _Conn_dist_1_1_to_dist_6_1 | Distributed Server 1 | Connection lost to Town Hall Server 1 - Link 1 |  |  |  | 0 | ARN | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:20.022 | _Conn_event_0_1_to_event_0_2 | State Library Server 1 | Connection lost to Server 2 - Link 0 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:20.022 | _Conn_event_0_1_to_event_0_2 | State Library Server 1 | Connection Connection lost to Server 2 - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:19.891 | _Conn_dist_1_1_to_dist_5_2 | Distributed Server 1 | Connection lost to State Library Server 2 - Link 0 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:19.891 | _Conn_dist_1_1_to_dist_5_2 | Distributed Server 1 | Connection lost to State Library Server 2 - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.10 08:49:19.891 | _Conn_dist_1_1_to_dist_6_1 | Distributed Server 1 | Connection lost to Town Hall Server 1 - Link 0 |  |  |  | 0 | ARN | Servers Comms
CAME UNACK Med | 2024.05.06 09:08:20.849 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:17.878 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:17.874 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Low | 2024.05.16 07:13:12.195 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.16 07:11:39.150 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.16 06:37:51.436 | AEN_DOR_B2_ESC_STAIRS_03_2 | Platform 1 west - double emergency door | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.15 23:17:54.989 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator stopped.(emergency brake fault) |  |  |  | 0 | AZC
CAME UNACK Low | 2024.05.15 23:08:21.005 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:08:21.005 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:07:15.002 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:07:15.002 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:05:07.001 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:05:07.001 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:04:06.103 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:04:06.103 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0001 | Escalator 1 Bank 1 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0002 | Escalator 2 Bank 2 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0003 | Escalator 3 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0005 | Escalator 5 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0007 | Escalator 7 Bank 5 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0008 | Escalator 8 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0009 | Escalator 9 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0010 | Escalator 10 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0011 | Escalator 11 Bank 7 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 23:00:27.226 | DMA_ESC_0012 | Escalator 12 Bank 7 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.15 13:51:44.182 | PKV_FCU_1207_MCV_01 | Fan Coil Unit - Chilled Water Valve | Modulated device position discrepancy fault alarm |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.726 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.725 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:16:24.723 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.15 13:11:10.471 | PKV_TEXB | Tunnel Ambient Temperature Control - Westbound | Tunnel B - Ambient Temperature Control Unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.15 12:54:08.345 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.15 11:23:31.696 | PKV_DOR_B4_PKV-S-01_2 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.15 11:19:14.803 | PKV_DOR_B4_PKV-S-01_3 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.15 10:04:18.080 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.15 10:04:14.081 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.15 09:48:41.101 | PKV_ESC_0009 | Escalator 9 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.15 09:47:27.103 | PKV_ESC_0008 | Escalator 8 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.15 09:02:07.955 | PKV_DOR_B4_PKV-S-01_1 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.15 07:32:01.078 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.14 16:49:22.617 | TSC-E-PSD-016 | Town Hall Platform 2 Zone 2 PSD 16 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.14 15:01:07.674 | PKV_DOR_B4_PKV-S-01_4 | West Emergency Stairs - Platform | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.14 14:33:09.925 | PKV_ESC_0007 | Escalator 7 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.14 13:23:13.971 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.14 13:15:55.101 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.14 11:10:35.956 | PKV-E-PSD-027 | Parkville Platform 2 Zone 3 PSD 27 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.14 09:25:03.092 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.14 09:25:03.092 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.13 17:47:27.031 | EPZ-FIP-0001 | Eastern Portal Main Fire Panel | Fire panels in the station have a fault |  |  |  | 0 | SDU | Fire Panel Fault
CAME UNACK Low | 2024.05.13 17:25:33.644 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 17:25:33.633 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 13:39:35.953 | PKV-W-PSD-004 | Parkville Platform 1 Zone 1 PSD 04 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 10:26:06.613 | TSC-W-PSD-016 | Town Hall Platform 1 Zone 2 PSD 16 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 09:51:34.145 | AEN-W-PSD-009 | Arden Platform 1 Zone 1 PSD 09 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 09:47:56.309 | TNC-W-PSD-025 | State Library Platform 1 Zone 3 PSD 25 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 09:27:40.307 | TNC-E-PSD-025 | State Library Platform 2 Zone 3 PSD 25 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.13 09:00:40.144 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.05.11 17:44:44.220 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.11 17:44:44.220 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.11 17:32:30.803 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.11 17:31:51.797 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.10 12:09:52.390 | PKV-SPE-0018 | B1, PKV-SPE-0018 Gas Meter Room 944-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.05.10 09:35:22.263 | DMA_SDP_0109_10_FG | Station Drainage Pump - Function Group | Station drainage pit not dropping! |  |  |  | 0 | AZC
CAME UNACK Low | 2024.05.10 08:49:20.799 | _ReduManager_2 | Town Hall Server 2 | Server 2 - Active - No connection to redundant peer |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Low | 2024.05.08 19:18:06.264 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.08 19:18:06.252 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.08 14:11:37.281 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.08 14:11:34.169 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.08 13:06:35.362 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 10:38:29.085 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Low | 2024.05.06 10:38:29.076 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Low | 2024.05.06 09:24:19.432 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:24:18.770 | TSC-E-PSD-009 | Town Hall Platform 2 Zone 1 PSD 09 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:12:44.004 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.963 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.937 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.908 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:37.638 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 09:12:37.580 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 09:08:50.121 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:49.343 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:48.560 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:42.286 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:41.504 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:39.183 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:38.414 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:16.052 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:07:56.289 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:07:34.198 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | Door status indicator fault |  |  |  | 0 | STL
CAME UNACK Low | 2024.05.06 09:07:33.965 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
WENT UNACK Med | 2024.05.15 15:43:10.077 | _AEN-BMS-PLC3 | MTARD:_AEN-BMS-PLC3. | Communications Fault - Arden Server 1 to Arden BMS 3 PLC |  |  | 2024.05.15 15:43:10.941 | 0 | ARN
WENT UNACK Med | 2024.05.15 15:42:42.410 | _AEN-BMS-PLC | Arden BMS PLC | Communications Fault - Arden Server 1 to Arden BMS PLC |  |  | 2024.05.15 15:42:49.197 | 0 | ARN
WENT UNACK Med | 2024.05.15 15:31:04.020 | _AEN-TVC-PLC_2 | Arden Server 2 | Communications Fault - Arden Server 2 to Arden TVCS PLC |  |  | 2024.05.15 15:31:04.069 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.930 | _Mod_Plc_2_2 | MTARD:_Mod_Plc_2_2. | Communications Fault - Arden Server 2 to Arden FDS Gateway |  |  | 2024.05.15 15:31:05.829 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.929 | _Mod_Plc_1_2 | Arden Server 2 | Communications Fault - Arden Server 2 to Arden PSD Servers |  |  | 2024.05.15 15:31:06.674 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.929 | _Mod_Plc_4_2 | MTARD:_Mod_Plc_4_2. | Communications Fault - Arden Server 2 to Arden EWIS |  |  | 2024.05.15 15:31:06.356 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.929 | _Mod_Plc_3_2 | MTARD:_Mod_Plc_3_2. | Communications Fault - Arden Server 2 to Arden EWIS |  |  | 2024.05.15 15:31:06.256 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.919 | _AEN-BMS-PLC_2 | Arden BMS PLC | Communications Fault - Arden Server 2 to Arden BMS PLC |  |  | 2024.05.15 15:31:11.274 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.919 | _AEN-BMS-PLC3_2 | MTARD:_AEN-BMS-PLC3_2. | Communications Fault - Arden Server 2 to Arden BMS 3 PLC |  |  | 2024.05.15 15:31:05.150 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.919 | _AEN-FDS-S7PLUS_2 | MTARD:_AEN-FDS-S7PLUS_2. | Communications Fault - Arden Server 2 to Arden FDS PLC |  |  | 2024.05.15 15:31:07.243 | 0 | PKV
WENT UNACK Med | 2024.05.15 15:29:40.919 | _PAE-BMS-PLC_2 | MTARD:_PAE-BMS-PLC_2. | Communications Fault - Arden Server 2 to Western Portal BMS PLC |  |  | 2024.05.15 15:31:06.178 | 0 | PKV
WENT UNACK Low | 2024.05.15 23:50:06.573 | _Mod_Plc_1_2 | Distributed Server 1 | Communications Fault - Distributed Server 2 to RSG |  |  | 2024.05.15 23:50:07.525 | 0 | THL | Servers Comms
WENT UNACK Low | 2024.05.15 15:31:03.236 | _ReduManager_2 | Arden Server 2 | Server 2 - Passive |  |  | 2024.05.15 15:31:13.427 | 0 | PKV
WENT UNACK Low | 2024.05.15 15:29:41.331 | _AEN-TVC-PLC_2 | Arden Server 2 | Link Failure - Arden Server 2 to Arden TVCS CPU 1 |  |  | 2024.05.15 15:31:04.069 | 0 | PKV
WENT UNACK Low | 2024.05.15 15:29:41.331 | _AEN-TVC-PLC_2 | Arden Server 2 | Link Failure - Arden Server 2 to Arden TVCS CPU 2 |  |  | 2024.05.15 15:31:04.110 | 0 | PKV
ACK High | 2024.05.06 09:09:56.866 | AEN-E-PED-002 | Arden Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! | 2024.05.07 11:11:31.394 | dominic_dlasselle |  | 0 | ARN | PED Opening
ACK High | 2024.05.06 09:08:17.159 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.05.07 11:11:28.284 | dominic_dlasselle |  | 0 | ARN | PED Opening
ACK High | 2024.05.06 09:07:53.952 | AEN-W-PSD-030 | Arden Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:25.224 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:50.397 | AEN-W-PSD-021 | Arden Platform 1 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:21.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:46.057 | AEN-W-PSD-010 | Arden Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:19.282 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:42.500 | AEN-W-PSD-001 | Arden Platform 1 Zone 1 PSD 01 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:16.395 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:42.056 | AEN-E-PSD-030 | Arden Platform 2 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:13.880 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:41.617 | AEN-E-PSD-029 | Arden Platform 2 Zone 3 PSD 29 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:11.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:41.176 | AEN-E-PSD-028 | Arden Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:08.959 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:40.736 | AEN-E-PSD-027 | Arden Platform 2 Zone 3 PSD 27 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:05.281 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:40.288 | AEN-E-PSD-026 | Arden Platform 2 Zone 3 PSD 26 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:02.688 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:39.848 | AEN-E-PSD-025 | Arden Platform 2 Zone 3 PSD 25 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:00.161 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:39.406 | AEN-E-PSD-024 | Arden Platform 2 Zone 3 PSD 24 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:56.360 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.966 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:53.690 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.524 | AEN-E-PSD-022 | Arden Platform 2 Zone 3 PSD 22 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:50.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.081 | AEN-E-PSD-021 | Arden Platform 2 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:46.885 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:37.633 | AEN-E-PSD-020 | Arden Platform 2 Zone 2 PSD 20 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:36.688 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:37.189 | AEN-E-PSD-019 | Arden Platform 2 Zone 2 PSD 19 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:05.878 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:36.748 | AEN-E-PSD-018 | Arden Platform 2 Zone 2 PSD 18 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:33.624 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:36.298 | AEN-E-PSD-017 | Arden Platform 2 Zone 2 PSD 17 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:28.595 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:35.859 | AEN-E-PSD-016 | Arden Platform 2 Zone 2 PSD 16 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:26.276 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:35.420 | AEN-E-PSD-015 | Arden Platform 2 Zone 2 PSD 15 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:23.623 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.980 | AEN-E-PSD-014 | Arden Platform 2 Zone 2 PSD 14 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:18.900 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.541 | AEN-E-PSD-013 | Arden Platform 2 Zone 2 PSD 13 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:21.491 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.099 | AEN-E-PSD-012 | Arden Platform 2 Zone 2 PSD 12 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:16.136 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:33.658 | AEN-E-PSD-011 | Arden Platform 2 Zone 2 PSD 11 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:12.867 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:33.212 | AEN-E-PSD-010 | Arden Platform 2 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:10.162 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK Med | 2024.05.13 17:47:26.270 | DMA-FIP-0002 | Anzac Station SHCIE Panel 2 | Power supply to gas supression panel fault | 2024.05.13 18:01:45.433 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.13 17:47:26.270 | DMA-FIP-0003 | Anzac Station SHCIE Panel 3 | Power supply to gas supression panel fault | 2024.05.13 17:59:50.913 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.13 17:47:26.270 | DMA-FIP-0004 | Anzac Station SHCIE Panel 4 | Power supply to gas supression panel fault | 2024.05.13 18:01:41.038 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.13 17:47:26.270 | DMA-FIP-0005 | Anzac Station SHCIE Panel 5 | Power supply to gas supression panel fault | 2024.05.13 17:59:59.864 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.13 17:47:26.268 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Power supply to fire panel fault | 2024.05.13 17:58:02.958 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.13 17:47:15.540 | DMA-C-01-EVAC | EWIS device for Anzac | EWIS fault | 2024.05.13 17:49:11.875 | himanshu_kakkad |  | 0 | AZC | CMS Interface testing in progress
ACK Med | 2024.05.06 11:54:12.166 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.05.06 12:03:26.229 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.06 11:54:12.159 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Med | 2024.05.06 10:38:29.113 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.110 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.108 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.106 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.104 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.102 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.101 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.099 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 09:10:37.753 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Emergency Intercom Activated Level 2 | 2024.05.10 13:20:22.767 | chris_lawson |  | 0 | AZC | Test in progress
ACK Med | 2024.05.06 09:08:34.594 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2024.05.06 09:08:34.583 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2024.05.06 09:08:34.544 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2024.05.06 09:08:30.972 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable | 2024.05.15 17:27:58.201 | himanshu_kakkad |  | 0 | SDU | TVCS Fans out of service
ACK Med | 2023.10.10 08:29:53.877 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Med | 2023.10.10 08:29:53.243 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Med | 2023.10.10 08:29:52.927 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | THL | Servers Comms
ACK Med | 2023.10.10 08:29:49.030 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Low | 2024.05.14 16:47:39.004 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault | 2024.05.14 21:30:22.567 | himanshu_kakkad |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.14 16:47:39.004 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault | 2024.05.14 21:30:22.509 | himanshu_kakkad |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.14 10:29:33.130 | PKV_LFT_0010 | Lift 10 BOH (B4 Basement to B1 Basement) | Lift General Fault | 2024.05.14 14:17:22.270 | chris_lawson |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.05.13 17:47:27.035 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Fire panels in the station have a fault | 2024.05.13 17:58:02.875 | himanshu_kakkad |  | 0 | AZC | Fire Panel Fault
ACK Low | 2024.05.13 09:59:29.110 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift monitoring lost | 2024.05.13 10:12:11.697 | fadi_duqman |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.13 09:44:26.108 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault | 2024.05.13 10:12:11.630 | fadi_duqman |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.13 07:36:30.057 | DMA_ESC_0001 | Escalator 1 Bank 1 (B2 Basement to B1 Basement) | Escalator communications lost | 2024.05.13 17:33:36.574 | himanshu_kakkad |  | 0 | AZC | Escalators out of service
ACK Low | 2024.05.10 14:42:41.810 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault | 2024.05.10 14:42:58.689 | paul_moseley |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.10 14:42:41.810 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.05.10 14:42:58.689 | paul_moseley |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.10 14:14:53.099 | AEN_DOR_B1_151-4_1 | Concourse east - back of house emergency corridor | Unauthorised access | 2024.05.10 14:16:10.529 | paul_moseley |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.09 08:07:59.254 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault | 2024.05.09 11:14:17.793 | emilio_ito |  | 0 | PKV | Fire Panel Fault
ACK Low | 2024.05.07 10:37:18.214 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift monitoring lost | 2024.05.15 20:20:25.682 | himanshu_kakkad |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.07 10:37:18.214 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault | 2024.05.15 20:20:25.651 | himanshu_kakkad |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.05.06 11:54:12.186 | _ReduManager | Distributed Server 1 | Server 1 - Set active automatically | 2024.05.06 12:03:12.642 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 10:38:29.082 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 10:38:29.074 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 09:12:44.076 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown | 2024.05.15 17:27:58.116 | himanshu_kakkad |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.05.06 09:12:44.048 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown | 2024.05.15 17:27:58.122 | himanshu_kakkad |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.05.06 09:12:37.455 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:12:37.328 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Door open too long | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:10:37.931 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault | 2024.05.10 13:20:22.737 | chris_lawson |  | 0 | AZC | General fault alarm as a result of loss of power