## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.05.21 08:40:27.453 | PKV-Z-4352 | ZONE 4352: B2, PKV-AJ-01 Unallocated Area 299-5 | Smoke or heat detected - fire unconfirmed! |  |  |  | 0 | PKV
CAME UNACK High | 2024.05.20 14:42:37.566 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.20 14:42:26.553 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:41:01.441 | SKP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.382 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.316 | SKP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.264 | SKP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:39:51.562 | TSC-W-PED-002 | Town Hall Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.20 11:39:51.547 | TSC-E-PED-002 | Town Hall Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.20 11:39:46.730 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.20 11:39:46.626 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.20 11:39:16.818 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.20 11:39:16.804 | TNC-E-PED-002 | State Library Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.20 11:39:11.392 | PKV-W-PED-002 | Parkville Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.20 11:39:11.379 | PKV-E-PED-002 | Parkville Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.20 11:37:21.333 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.20 11:37:05.406 | TSC-W-PED-001 | Town Hall Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.20 11:37:05.387 | TSC-E-PED-001 | Town Hall Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.20 11:36:58.729 | TNC-W-PED-001 | State Library Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.20 11:36:58.712 | TNC-E-PED-001 | State Library Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.20 11:36:46.457 | PKV-W-PED-001 | Parkville Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.20 11:36:46.444 | PKV-E-PED-001 | Parkville Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.20 11:36:37.323 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK High | 2024.05.20 11:36:32.084 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK High | 2024.05.20 11:36:31.964 | TSC-W-PSD-030 | Town Hall Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.20 11:36:20.196 | TSC-W-PSD-010 | Town Hall Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.20 11:36:13.988 | PKV-W-PSD-004 | Parkville Platform 1 Zone 1 PSD 04 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.20 11:36:10.790 | PKV-E-PSD-027 | Parkville Platform 2 Zone 3 PSD 27 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.20 11:35:50.579 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:49.862 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:47.957 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:47.478 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:46.985 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:44.005 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:43.996 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:43.989 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.20 11:35:43.980 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 14:42:37.566 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:42:04.525 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Power supply to fire panel fault |  |  |  | 0 | AZC | CMS Interface testing in progress
CAME UNACK Med | 2024.05.20 11:38:23.007 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:38:12.663 | DMA-C-01-EVAC | EWIS device for Anzac | EWIS fault |  |  |  | 0 | AZC | CMS Interface testing in progress
CAME UNACK Med | 2024.05.20 11:37:01.190 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.05.20 11:37:01.179 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.05.20 11:36:47.215 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:36:47.211 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:36:44.454 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:36:44.450 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:35:57.887 | DMA-FIP-0004 | Anzac Station SHCIE Panel 4 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | CMS Interface testing in progress
CAME UNACK Med | 2024.05.20 11:35:57.455 | DMA-FIP-0003 | Anzac Station SHCIE Panel 3 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | CMS Interface testing in progress
CAME UNACK Med | 2024.05.20 11:35:57.031 | DMA-FIP-0002 | Anzac Station SHCIE Panel 2 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | CMS Interface testing in progress
CAME UNACK Med | 2024.05.20 11:35:27.847 | PKV-S-STN | Parkville Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.21 10:20:20.976 | DMA-SPE-0248 | B1, DMA-SPE-0248 CONC UNPAID AREA 102-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 10:09:04.885 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 10:09:02.212 | _ReduManager | Distributed Server 1 | Server 1 - Preferred active |  |  |  | 0 | ARN
CAME UNACK Low | 2024.05.21 10:09:00.081 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.012 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.011 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.21 09:58:33.009 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU
CAME UNACK Low | 2024.05.21 09:54:38.061 | DMA-SPE-0831 | B1, DMA-SPE-0831 Escalator 11 (B1 Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:38.061 | DMA-SPE-0832 | B1, DMA-SPE-0832 Escalator 12 (B1 Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:38.061 | DMA-FPD-0019 | B1, DMA-FPD-0019 FCU-1123 LFT-07 S/A | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:38.061 | DMA-FPD-0020 | B1, DMA-FPD-0020 FCU-1124 LFT-07 S/A | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:37.957 | DMA-SPE-0811 | GF, DMA-SPE-0811 Escalator 11 (GF Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:37.957 | DMA-SPE-0812 | GF, DMA-SPE-0812 Escalator 12 (GF Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0166 | B1, DMA-SPE-0166 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0167 | B1, DMA-SPE-0167 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0168 | B1, DMA-SPE-0168 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0722 | B1, DMA-SPE-0722 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0723 | B1, DMA-SPE-0723 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:35.810 | DMA-SPE-0725 | B1, DMA-SPE-0725 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.929 | DMA-SPE-0170 | B1, DMA-SPE-0170 FIRE LOBBY C/S 406-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.929 | DMA-SPE-0721 | B1, DMA-SPE-0721 FIRE LOBBY 406-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.929 | DMA-SPE-0724 | B1, DMA-SPE-0724 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.928 | DMA-SPE-0004 | B1, DMA-SPE-0004 FIELD DEV ROOM 710-6 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.928 | DMA-SPE-0005 | B1, DMA-SPE-0005 HVAC PLANT ROOM 811-8 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:34.928 | DMA-SPE-0006 | B1, DMA-SPE-0006 HVAC PLANT ROOM 811-8 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:04.929 | DMA-SPE-0244 | B1, DMA-SPE-0244 CONC UNPAID AREA 102-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:04.929 | DMA-SPE-0245 | B1, DMA-SPE-0245 CONC UNPAID AREA 102-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:04.929 | DMA-SPE-0246 | B1, DMA-SPE-0246 CONC UNPAID AREA 102-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:04.929 | DMA-SPE-0247 | B1, DMA-SPE-0247 CONC UNPAID AREA 102-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:04.877 | DMA-SPE-0169 | B1, DMA-SPE-0169 FIRE ESCAPE C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:54:01.937 | DMA-SPE-0007 | B1, DMA-SPE-0007 WATER METER ROOM 884-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:32:55.877 | DMA-SPE-0326 | B1, DMA-SPE-0326 CONC PAID AREA 103-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.21 09:32:45.676 | EPZ-FIP-0001 | Eastern Portal Main Fire Panel | Fire panels in the station have a fault |  |  |  | 0 | SDU | Fire Panel Fault
CAME UNACK Low | 2024.05.21 08:40:28.398 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 08:40:18.390 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 08:39:39.856 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 08:32:16.871 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 07:59:26.410 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 07:59:26.410 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 07:46:35.826 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.21 07:23:41.390 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:12.082 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:10.607 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:10.373 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:09.770 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:09.544 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:07.284 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:07.088 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:05.520 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:42:04.140 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | AZC | Fire Panel Fault
CAME UNACK Low | 2024.05.20 11:40:59.840 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.814 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.786 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.771 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.746 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.732 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.703 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.676 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:53.391 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.20 11:40:53.378 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.20 11:40:31.169 | WPZ-FIP-0001 | Western Portal Main Fire Panel | Fire panels in the station have a fault |  |  |  | 0 | SDU | Fire Panel Fault
CAME UNACK Low | 2024.05.20 11:39:52.026 | PKV-SPE-0018 | B1, PKV-SPE-0018 Gas Meter Room 944-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.05.20 11:39:43.737 | DMA_ESC_0012 | Escalator 12 Bank 7 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:41.444 | DMA_ESC_0011 | Escalator 11 Bank 7 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:38.899 | DMA_ESC_0010 | Escalator 10 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:36.789 | DMA_ESC_0009 | Escalator 9 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:34.649 | DMA_ESC_0008 | Escalator 8 Bank 6 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:32.562 | DMA_ESC_0007 | Escalator 7 Bank 5 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:30.472 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:28.351 | DMA_ESC_0005 | Escalator 5 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:26.240 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:24.083 | DMA_ESC_0003 | Escalator 3 Bank 3 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:21.975 | DMA_ESC_0002 | Escalator 2 Bank 2 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:19.781 | DMA_ESC_0001 | Escalator 1 Bank 1 (B2 Basement to B1 Basement) | Escalator fire response isolated |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.20 11:39:07.244 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:07.090 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:06.834 | PKV_LFT_0010 | Lift 10 BOH (B4 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:06.572 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:06.422 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:06.268 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:06.120 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.966 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.814 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.661 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.399 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.252 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:05.097 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:04.942 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:04.769 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:04.621 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:04.467 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:04.208 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:39:03.104 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | PKV | Fire Panel Fault
CAME UNACK Low | 2024.05.20 11:37:49.465 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.20 11:37:16.533 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:15.771 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:15.006 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:14.241 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:13.477 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:12.716 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:11.955 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:08.899 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:08.137 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:07.369 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:06.603 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:05.820 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:05.051 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.20 11:37:01.467 | PKV_TEXB | Tunnel Ambient Temperature Control - Westbound | Tunnel B - Ambient Temperature Control Unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.20 11:36:36.736 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:31.515 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:22.801 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:00.710 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | Door status indicator fault |  |  |  | 0 | STL
CAME UNACK Low | 2024.05.20 11:36:00.473 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
WENT UNACK Low | 2024.05.21 10:50:31.352 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Unauthorised access |  |  | 2024.05.21 10:50:37.407 | 0 | ARN | Door forced open without using a valid card
WENT UNACK Low | 2024.05.21 09:52:21.783 | _Mod_Plc_1_2 | Distributed Server 1 | Communications Fault - Distributed Server 2 to RSG |  |  | 2024.05.21 10:12:35.921 | 0 | THL | Servers Comms
ACK High | 2024.05.20 11:38:22.078 | AEN-W-PED-002 | Arden Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! | 2024.05.21 09:42:54.436 | harsimran_virk |  | 0 | ARN | PED Opening
ACK High | 2024.05.20 11:38:22.062 | AEN-E-PED-002 | Arden Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! | 2024.05.21 09:43:00.172 | harsimran_virk |  | 0 | ARN | PED Opening
ACK High | 2024.05.20 11:36:43.639 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.05.21 09:43:02.788 | harsimran_virk |  | 0 | ARN | PED Opening
ACK High | 2024.05.20 11:36:43.624 | AEN-E-PED-001 | Arden Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.05.21 09:43:06.872 | harsimran_virk |  | 0 | ARN | PED Opening
ACK High | 2024.05.20 11:36:20.068 | AEN-W-PSD-030 | Arden Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:10.210 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:16.396 | AEN-W-PSD-021 | Arden Platform 1 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:16.772 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:11.965 | AEN-W-PSD-010 | Arden Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:19.309 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:08.360 | AEN-W-PSD-001 | Arden Platform 1 Zone 1 PSD 01 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:03.086 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:07.916 | AEN-E-PSD-030 | Arden Platform 2 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:04.696 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:07.471 | AEN-E-PSD-029 | Arden Platform 2 Zone 3 PSD 29 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:06.305 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:07.023 | AEN-E-PSD-028 | Arden Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:09.228 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:06.570 | AEN-E-PSD-027 | Arden Platform 2 Zone 3 PSD 27 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:13.697 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:06.124 | AEN-E-PSD-026 | Arden Platform 2 Zone 3 PSD 26 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:15.881 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:05.660 | AEN-E-PSD-025 | Arden Platform 2 Zone 3 PSD 25 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:17.853 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:05.212 | AEN-E-PSD-024 | Arden Platform 2 Zone 3 PSD 24 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:19.824 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:04.760 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:21.281 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:04.300 | AEN-E-PSD-022 | Arden Platform 2 Zone 3 PSD 22 | PSD Unscheduled Door Opening! | 2024.05.21 09:52:18.107 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:03.846 | AEN-E-PSD-021 | Arden Platform 2 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.21 09:56:16.109 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:03.404 | AEN-E-PSD-020 | Arden Platform 2 Zone 2 PSD 20 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:29.874 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:02.960 | AEN-E-PSD-019 | Arden Platform 2 Zone 2 PSD 19 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:27.187 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:02.513 | AEN-E-PSD-018 | Arden Platform 2 Zone 2 PSD 18 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:34.472 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:02.070 | AEN-E-PSD-017 | Arden Platform 2 Zone 2 PSD 17 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:32.389 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:01.625 | AEN-E-PSD-016 | Arden Platform 2 Zone 2 PSD 16 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:38.752 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:01.181 | AEN-E-PSD-015 | Arden Platform 2 Zone 2 PSD 15 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:41.572 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:00.734 | AEN-E-PSD-014 | Arden Platform 2 Zone 2 PSD 14 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:44.027 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:36:00.288 | AEN-E-PSD-013 | Arden Platform 2 Zone 2 PSD 13 | PSD Unscheduled Door Opening! | 2024.05.21 09:47:45.336 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:35:59.833 | AEN-E-PSD-012 | Arden Platform 2 Zone 2 PSD 12 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:53.595 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:35:59.383 | AEN-E-PSD-011 | Arden Platform 2 Zone 2 PSD 11 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:57.348 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 11:35:58.924 | AEN-E-PSD-010 | Arden Platform 2 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.21 09:43:59.900 | harsimran_virk |  | 0 | ARN | PSD Opening
ACK High | 2024.05.20 08:23:30.503 | _Driver2 | MTTHL:_Driver2. | Driver overloaded | 2024.05.20 15:17:54.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.13 17:25:33.702 | _Driver1_2 | MTAZC:_Driver1_2. | Driver overloaded | 2024.05.17 08:14:22.995 | dominic_dlasselle |  | 0 | ARN | Servers Comms
ACK High | 2024.05.10 08:49:20.968 | _Driver2_2 | MTTHL:_Driver2_2. | Driver overloaded | 2024.05.20 15:17:59.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.08 09:24:26.938 | _Driver1_2 | MTARD:_Driver1_2. | Driver overloaded | 2024.05.20 15:17:40.384 | eric_maddocks |  | 0 | PKV | Servers Comms
ACK Med | 2024.05.20 12:06:59.071 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.068 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.066 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.064 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.062 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.059 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.057 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.054 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.001 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.20 12:06:58.974 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Med | 2024.05.20 12:03:55.569 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:55.564 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:55.560 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.20 12:03:54.231 | _Mod_Plc_4_2 | MTTHL:_Mod_Plc_4_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:03:54.227 | _Mod_Plc_3_2 | MTTHL:_Mod_Plc_3_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2024.05.20 15:18:07.088 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:03:54.223 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway | 2024.05.20 15:18:07.088 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:15.441 | _Mod_Plc_4_2 | MTAZC:_Mod_Plc_4_2. | Communications Fault - Anzac Server 2 to Anzac EWIS | 2024.05.20 15:18:27.824 | eric_maddocks |  | 0 | ARN
ACK Med | 2024.05.20 12:03:15.441 | _Mod_Plc_3_2 | MTAZC:_Mod_Plc_3_2. | Communications Fault - Anzac Server 2 to Anzac EWIS | 2024.05.20 15:18:27.824 | eric_maddocks |  | 0 | ARN
ACK Med | 2024.05.20 12:03:14.933 | _Mod_Plc_1_2 | Anzac Server 2 | Communications Fault - Anzac Server 2 to Anzac PSD | 2024.05.20 15:18:07.116 | eric_maddocks |  | 0 | ARN
ACK Med | 2024.05.20 12:02:23.523 | _Mod_Plc_4 | MTAZC:_Mod_Plc_4. | Communications Fault - Anzac Server 1 to Anzac EWIS | 2024.05.20 15:18:27.824 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:02:23.482 | _Mod_Plc_3 | MTAZC:_Mod_Plc_3. | Communications Fault - Anzac Server 1 to Anzac EWIS | 2024.05.20 15:18:07.116 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:02:23.399 | _Mod_Plc_1 | Anzac Server 1 | Communications Fault - Anzac Server 1 to Anzac PSD | 2024.05.20 15:18:07.116 | eric_maddocks |  | 0 | AZC
ACK Low | 2024.05.21 09:50:11.517 | AEN_DOR_B1_151-4_1 | Concourse east - back of house emergency corridor | Unauthorised access | 2024.05.21 09:52:39.145 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 12:06:59.010 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.05.20 12:06:59.006 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.20 12:06:58.995 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.05.20 12:06:58.990 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.20 11:40:53.209 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.05.21 09:43:32.566 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 11:40:53.176 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Door open too long | 2024.05.21 09:43:32.566 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 11:39:46.751 | AEN-SPE-0404 | B1, AEN-SPE-0404, 151-10 BOH Corridor | Heat or smoke detector fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.05.20 11:38:18.110 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.20 11:38:17.926 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.20 11:38:16.922 | AEN-FIP-0001 | Arden Main Fire Panel | Fire panels in the station have a fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Fire Panel Fault
ACK Low | 2024.05.20 11:37:06.086 | AEN_ESC_0007 | Escalator 7 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.20 11:37:05.402 | AEN_ESC_0006 | Escalator 6 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.20 11:37:04.724 | AEN_ESC_0005 | Escalator 5 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service