## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.06.09 12:17:50.992 | SYP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.07 16:53:04.990 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.07 16:21:32.370 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.07 16:20:58.355 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.07 16:20:32.374 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.07 16:20:26.348 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.07 16:19:25.358 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.07 16:19:25.358 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.06 22:43:22.274 | TSC-W-PSD-029 | Town Hall Platform 1 Zone 3 PSD 29 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.06.06 22:43:22.251 | TSC-W-PSD-011 | Town Hall Platform 1 Zone 2 PSD 11 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.06.06 21:46:02.249 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.06.06 20:29:56.249 | TNC-E-PED-001 | State Library Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.06.05 18:14:54.704 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.05 18:14:18.712 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.05 18:13:20.702 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.05 18:13:04.701 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.05 09:55:12.511 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.05 09:55:12.511 | PKV_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.03 10:03:13.630 | AEN_ROL_RNERV_W | West Tunnel RNERV Roller Door | RNERV crane arm extended over tracks! |  |  |  | 0 | SDU
CAME UNACK High | 2024.06.03 10:01:16.559 | DMA-W-PED-002 | Anzac Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK High | 2024.06.03 10:01:16.545 | DMA-E-PED-002 | Anzac Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK High | 2024.06.03 09:59:12.828 | DMA-W-PED-001 | Anzac Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK High | 2024.06.03 09:59:12.814 | DMA-E-PED-001 | Anzac Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK High | 2024.06.03 09:58:26.306 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK Med | 2024.06.11 07:11:06.679 | PKV_FCU_1213_14_FG | Fan Coil Unit - Function Group | Cooling unavailable! |  |  |  | 0 | PKV
CAME UNACK Med | 2024.06.07 16:20:58.355 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.07 16:20:32.374 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.05 18:14:18.712 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.05 18:13:04.701 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.05 17:32:57.701 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.04 08:42:49.681 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.04 08:42:44.680 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.03 10:50:15.738 | _Driver1_2 | Anzac Server 2 | PSS2 S7 Driver 1 overloaded (TVCS PLC) |  |  |  | 0 | ARN
CAME UNACK Med | 2024.06.03 10:50:12.774 | _Mod_Plc_1 | Anzac Server 1 | Communications Fault - Anzac Server 1 to Anzac PSD |  |  |  | 0 | AZC
CAME UNACK Med | 2024.06.03 10:49:53.702 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:53.696 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:53.691 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:52.195 | _Mod_Plc_4_2 | MTTHL:_Mod_Plc_4_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS |  |  |  | 0 | AZC
CAME UNACK Med | 2024.06.03 10:49:52.190 | _Mod_Plc_3_2 | MTTHL:_Mod_Plc_3_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS |  |  |  | 0 | AZC
CAME UNACK Med | 2024.06.03 10:49:52.185 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:38.106 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Communications Fault - State Library Server 2 to State Library TVCS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:38.097 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Communications Fault - State Library Server 1 to State Library TVCS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.239 | _TNC-FDS-S7PLUS_2 | MTSTL:_TNC-FDS-S7PLUS_2. | Communications Fault - State Library Server 2 to State Library FDS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.238 | _TNC-FDS-S7PLUS | MTSTL:_TNC-FDS-S7PLUS. | Communications Fault - State Library Server 1 to State Library FDS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.236 | _TNC-BMS-PLC3_2 | MTSTL:_TNC-BMS-PLC3_2. | Communications Fault - State Library Server 2 to State Library BMS Gateway PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.234 | _TNC-BMS-PLC3 | MTSTL:_TNC-BMS-PLC3. | Communications Fault - State Library Server 1 to State Library BMS Gateway PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.232 | _TNC-BMS-PLC_2 | MTSTL:_TNC-BMS-PLC_2. | Communications Fault - State Library Server 2 to State Library BMS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.229 | _TNC-BMS-PLC | MTSTL:_TNC-BMS-PLC. | Communications Fault - State Library Server 1 to State Library BMS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.969 | _Mod_Plc_4_2 | MTSTL:_Mod_Plc_4_2. | Communications Fault - State Library Server 2 to State Library EWIS |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.966 | _Mod_Plc_4 | MTSTL:_Mod_Plc_4. | Communications Fault - State Library Server 1 to State Library EWIS |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.964 | _Mod_Plc_3_2 | MTSTL:_Mod_Plc_3_2. | Communications Fault - State Library Server 2 to State Library EWIS |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.963 | _Mod_Plc_3 | MTSTL:_Mod_Plc_3. | Communications Fault - State Library Server 1 to State Library EWIS |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.961 | _Mod_Plc_2_2 | MTSTL:_Mod_Plc_2_2. | Communications Fault - State Library Server 2 to State Library FDS Gateway |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.959 | _Mod_Plc_2 | MTSTL:_Mod_Plc_2. | Communications Fault - State Library Server 1 to State Library FDS Gateway |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 09:57:47.739 | TSC-S-STN | Town Hall Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.11 04:31:51.586 | AEN_DOR_GF_246-1_2 | Ground floor west - loading dock 2 | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.06.08 07:27:24.841 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.08 07:25:34.572 | PKV_DOR_B1_PKV-S-02_2 | Security Door (B1 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.07 16:19:28.421 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 15:48:10.466 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 15:47:55.603 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 13:39:10.392 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 13:25:59.574 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | PKV | Fire Panel Fault
CAME UNACK Low | 2024.06.07 13:24:06.778 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 13:23:48.780 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 13:23:35.775 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 13:22:46.772 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 12:42:30.941 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.07 12:38:01.514 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 11:09:14.703 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.07 11:09:07.550 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 14:23:58.497 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 14:23:58.497 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 13:49:21.009 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:21.009 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:21.009 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:21.009 | PKV_ESC_0007 | Escalator 7 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.993 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.993 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.993 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.887 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.887 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.887 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.887 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.886 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:20.886 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:17.894 | PKV_ESC_0008 | Escalator 8 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:17.894 | PKV_ESC_0009 | Escalator 9 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 13:49:17.894 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.06 09:44:04.735 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 09:34:38.635 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 09:34:38.635 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 09:18:29.565 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 07:02:39.481 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 06:53:07.433 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 06:53:07.433 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 06:53:07.433 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 06:53:07.433 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.06 06:53:06.434 | SDU_TEP_0305_06_DS | Tunnel Drainage Pump - Duty Selection | All devices unavailable |  |  |  | 0 | AZC
CAME UNACK Low | 2024.06.06 06:53:06.406 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:48:52.660 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:48:42.662 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:38:08.639 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:38:01.572 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:34:18.644 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 20:34:11.570 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.05 14:25:01.628 | PKV_DOR_B2_PKV-S-03_3 | Security Door (B2 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 19:53:07.226 | PKV_DOR_GF_PKV-S-03_1 | Security Door (PUBLIC REALM WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 14:39:10.658 | PKV_DOR_GF_PKV-S-03_2 | Security Door (PUBLIC REALM WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 13:30:24.793 | PKV_DOR_B3_PKV-S-01_2 | Security Door (B3 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.913 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.04 11:37:27.910 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU
CAME UNACK Low | 2024.06.04 09:59:00.155 | PKV_DOR_B2_PKV-S-03_1 | Security Door (B2 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 09:56:34.724 | PKV_DOR_B4_PKV-S-01_4 | West Emergency Stairs - Platform | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.04 08:56:20.736 | AEN_TEXA | Tunnel Ambient Temperature Control - Eastbound | Temperature Sensors A - Discrepancy |  |  |  | 0 | SDU | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.03 10:49:38.103 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Link Failure - State Library Server 2 to State Library TVCS CPU 2 |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.03 10:49:38.099 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Link Failure - State Library Server 2 to State Library TVCS CPU 1 |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.03 10:49:38.092 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Link Failure - State Library Server 1 to State Library TVCS CPU 2 |  |  |  | 0 | STL
CAME UNACK Low | 2024.06.03 10:49:38.089 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Link Failure - State Library Server 1 to State Library TVCS CPU 1 |  |  |  | 0 | STL
CAME UNACK Low | 2024.06.03 10:47:20.619 | _ReduManager | Distributed Server 1 | Server 1 - Set active automatically |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.06.03 10:03:20.641 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.03 10:03:20.602 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.03 10:03:20.574 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.03 10:03:20.546 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.03 10:01:08.368 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.03 09:58:28.628 | TSC-E-PSD-016 | Town Hall Platform 2 Zone 2 PSD 16 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.06.03 09:58:24.519 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.06.03 09:58:19.119 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
WENT UNACK Med | 2024.06.07 16:41:21.941 | _PKV-BMS-PLC_2 | MTPKV:_PKV-BMS-PLC_2. | Communications Fault - Parkville Server 2 to Parkville BMS PLC |  |  | 2024.06.07 16:42:03.163 | 0 | STL
WENT UNACK Med | 2024.06.07 16:41:21.940 | _PKV-BMS-PLC | MTPKV:_PKV-BMS-PLC. | Communications Fault - Parkville Server 1 to Parkville BMS PLC |  |  | 2024.06.07 16:42:03.156 | 0 | PKV
WENT UNACK Med | 2024.06.07 12:55:11.060 | _PDM-BMS-PLC_2 | MTAZC:_PDM-BMS-PLC_2. | Communications Fault - Anzac Server 2 to Eastern Portal BMS PLC |  |  | 2024.06.07 12:57:59.045 | 0 | ARN
WENT UNACK Med | 2024.06.07 12:55:07.717 | _PDM-BMS-PLC | MTAZC:_PDM-BMS-PLC. | Communications Fault - Anzac Server 1 to Eastern Portal BMS PLC |  |  | 2024.06.07 12:57:55.049 | 0 | AZC
WENT UNACK Med | 2024.06.07 01:06:14.443 | _Mod_Plc_1_2 | Parkville Server 2 | Communications Fault - Parkville Server 2 to Parkville PSD Servers |  |  | 2024.06.07 01:06:15.444 | 0 | STL
WENT UNACK Med | 2024.06.06 22:47:29.484 | _SYP-TIAS-PLC_2 | MTDIST:_SYP-TIAS-PLC_2. | Communications Fault - Dist Server 2 to SYP TIAS PLC |  |  | 2024.06.06 22:48:11.135 | 0 | THL
WENT UNACK Med | 2024.06.06 22:47:11.219 | _SYP-TIAS-PLC | MTDIST:_SYP-TIAS-PLC. | Communications Fault - Dist Server 1 to SYP TIAS PLC |  |  | 2024.06.06 22:47:53.143 | 0 | ARN
WENT UNACK Med | 2024.06.06 14:52:58.463 | _Mod_Plc_2 | MTPKV:_Mod_Plc_2. | Communications Fault - Parkville Server 1 to Parkville FDS Gateway |  |  | 2024.06.06 14:53:02.586 | 0 | STL
WENT UNACK Med | 2024.06.06 12:34:49.031 | _DMA-TVC-PLC_2 | MTAZC:_DMA-TVC-PLC_2. | Communication Fault - Anzac Server 2 to Anzac TVCS PLC |  |  | 2024.06.06 12:35:19.113 | 0 | ARN
WENT UNACK Med | 2024.06.06 12:34:41.436 | _DMA-TVC-PLC | MTAZC:_DMA-TVC-PLC. | Communications Fault - Anzac Server 1 to Anzac TVCS PLC |  |  | 2024.06.06 12:35:11.498 | 0 | AZC
WENT UNACK Med | 2024.06.06 12:34:26.903 | _DMA-BMS-PLC_2 | MTAZC:_DMA-BMS-PLC_2. | Communications Fault - Anzac Server 2 to Anzac BMS PLC |  |  | 2024.06.06 12:34:31.590 | 0 | ARN
WENT UNACK Med | 2024.06.06 12:34:23.560 | _DMA-BMS-PLC3 | MTAZC:_DMA-BMS-PLC3. | Communications Fault - Anzac Server 1 to Anzac BMS Gateway PLC |  |  | 2024.06.06 12:34:27.537 | 0 | AZC
WENT UNACK Med | 2024.06.06 06:52:43.863 | _DMA-BMS-PLC | MTAZC:_DMA-BMS-PLC. | Communications Fault - Anzac Server 1 to Anzac BMS PLC |  |  | 2024.06.06 06:52:47.790 | 0 | AZC
WENT UNACK Med | 2024.06.05 13:05:54.617 | _AEN-BMS-PLC3 | MTARD:_AEN-BMS-PLC3. | Communications Fault - Arden Server 1 to Arden BMS Gateway PLC |  |  | 2024.06.05 13:05:54.803 | 0 | ARN
WENT UNACK Med | 2024.06.05 13:03:17.744 | _AEN-TVC-PLC_2 | Arden Server 2 | Communications Fault - Arden Server 2 to Arden TVCS PLC |  |  | 2024.06.05 13:06:03.417 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:03:17.728 | _AEN-TVC-PLC | Arden Server 1 | Communications Fault - Arden Server 1 to Arden TVCS PLC |  |  | 2024.06.05 13:05:46.289 | 0 | ARN
WENT UNACK Med | 2024.06.05 13:03:17.524 | _PKV-TVC-PLC_2 | MTPKV:_PKV-TVC-PLC_2. | Communications Fault - Parkville Server 2 to Parkville TVCS PLC |  |  | 2024.06.05 13:05:37.580 | 0 | STL
WENT UNACK Med | 2024.06.05 13:03:17.522 | _PKV-TVC-PLC | MTPKV:_PKV-TVC-PLC. | Communications Fault - Parkville Server 1 to Parkville TVCS PLC |  |  | 2024.06.05 13:05:50.904 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:03:17.067 | _PKV-BMS-PLC3_2 | MTPKV:_PKV-BMS-PLC3_2. | Communications Fault - Parkville Server 2 to Parkville BMS Gateway PLC |  |  | 2024.06.05 13:06:05.050 | 0 | STL
WENT UNACK Med | 2024.06.05 13:03:14.957 | _PAE-BMS-PLC_2 | MTARD:_PAE-BMS-PLC_2. | Communications Fault - Arden Server 2 to Western Portal BMS PLC |  |  | 2024.06.05 13:06:02.050 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:03:13.745 | _AEN-BMS-PLC_2 | Arden BMS PLC | Communications Fault - Arden Server 2 to Arden BMS PLC |  |  | 2024.06.05 13:06:01.155 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:03:13.745 | _AEN-BMS-PLC3_2 | MTARD:_AEN-BMS-PLC3_2. | Communications Fault - Arden Server 2 to Arden BMS Gateway PLC |  |  | 2024.06.05 13:06:01.054 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:02:59.941 | _PKV-BMS-PLC3 | MTPKV:_PKV-BMS-PLC3. | Communications Fault - Parkville Server 1 to Parkville BMS Gateway PLC |  |  | 2024.06.05 13:05:47.044 | 0 | PKV
WENT UNACK Med | 2024.06.05 13:02:59.224 | _DMA-BMS-PLC3_2 | MTAZC:_DMA-BMS-PLC3_2. | Communications Fault - Anzac Server 2 to Anzac BMS Gateway PLC |  |  | 2024.06.05 13:05:47.981 | 0 | ARN
WENT UNACK Med | 2024.06.05 13:02:59.184 | _AEN-BMS-PLC | Arden BMS PLC | Communications Fault - Arden Server 1 to Arden BMS PLC |  |  | 2024.06.05 13:05:47.178 | 0 | ARN
WENT UNACK Med | 2024.06.05 13:02:59.101 | _PAE-BMS-PLC | MTARD:_PAE-BMS-PLC. | Communications Fault - Arden Server 1 to Western Portal BMS PLC |  |  | 2024.06.05 13:05:47.062 | 0 | ARN
WENT UNACK Med | 2024.06.04 08:54:45.339 | DMA_AENComm | Arden TVCS PLC | HCS/ATS communication fault |  |  | 2024.06.04 08:56:13.358 | 0 | AZC | Comms fault to be investigated
WENT UNACK Med | 2024.06.03 16:42:15.430 | _Mod_Plc_2_2 | MTPKV:_Mod_Plc_2_2. | Communications Fault - Parkville Server 2 to Parkville FDS Gateway |  |  | 2024.06.03 16:42:20.080 | 0 | STL
WENT UNACK Med | 2024.06.03 15:40:46.547 | _Mod_Plc_2 | MTAZC:_Mod_Plc_2. | Communications Fault - Anzac Server 1 to Anzac FDS Gateway |  |  | 2024.06.03 15:41:49.337 | 0 | ARN
WENT UNACK Med | 2024.06.03 15:40:46.546 | _Mod_Plc_2_2 | MTAZC:_Mod_Plc_2_2. | Communications Fault - Anzac Server 2 to Anzac FDS Gateway |  |  | 2024.06.03 15:41:49.357 | 0 | ARN
WENT UNACK Low | 2024.06.11 07:07:47.236 | _Mod_Plc_1_2 | Distributed Server 1 | Communications Fault - Distributed Server 2 to RSG |  |  | 2024.06.11 07:07:48.103 | 0 | THL
WENT UNACK Low | 2024.06.05 13:03:17.723 | _AEN-TVC-PLC | Arden Server 1 | Link Failure - Arden Server 1 to Arden TVCS CPU 1 |  |  | 2024.06.05 13:05:46.289 | 0 | ARN
WENT UNACK Low | 2024.06.05 13:03:17.524 | _PKV-TVC-PLC_2 | MTPKV:_PKV-TVC-PLC_2. | Link Failure - Parkville Server 2 to Parkville TVCS CPU 1 |  |  | 2024.06.05 13:05:37.580 | 0 | STL
WENT UNACK Low | 2024.06.05 13:02:56.228 | _AEN-TVC-PLC | Arden Server 1 | Link Failure - Arden Server 1 to Arden TVCS CPU 2 |  |  | 2024.06.05 13:05:46.289 | 0 | ARN
ACK High | 2024.06.03 09:58:06.706 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! | 2024.06.04 08:53:46.364 | sergio_paniagua |  | 0 | PKV | TVCS Fans out of service
ACK High | 2024.06.03 09:58:06.239 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! | 2024.06.04 08:53:58.916 | sergio_paniagua |  | 0 | PKV | TVCS Fans out of service
ACK High | 2024.06.03 09:58:05.771 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! | 2024.06.04 08:41:47.122 | sergio_paniagua |  | 0 | PKV | TVCS Fans out of service
ACK High | 2024.05.20 08:23:30.503 | _Driver2 | MTTHL:_Driver2. | Driver overloaded | 2024.05.20 15:17:54.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.10 08:49:20.968 | _Driver2_2 | MTTHL:_Driver2_2. | Driver overloaded | 2024.05.20 15:17:59.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.06.03 10:48:16.685 | _Driver1_2 | MTARD:_Driver1_2. | PSS2 S7 Driver 1 overloaded (TVCS PLC) | 2024.06.04 08:54:10.389 | sergio_paniagua |  | 0 | PKV
ACK Med | 2024.06.03 10:47:25.339 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.338 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.337 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.336 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.335 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.334 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.333 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.331 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.305 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.06.03 10:47:25.290 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Med | 2024.06.03 09:59:08.939 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable | 2024.06.04 08:41:46.882 | sergio_paniagua |  | 0 | SDU | TVCS Fans out of service
ACK Med | 2024.06.03 09:59:08.936 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable | 2024.06.04 08:41:46.976 | sergio_paniagua |  | 0 | SDU | TVCS Fans out of service
ACK Low | 2024.06.06 06:53:07.433 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault | 2024.06.06 14:34:20.861 | chris_lawson |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.06.06 06:53:06.406 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault | 2024.06.06 14:34:20.825 | chris_lawson |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.06.05 14:59:30.636 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift monitoring lost | 2024.06.05 15:01:20.385 | emilio_ito |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.06.05 05:42:07.565 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.06.05 15:01:02.765 | emilio_ito |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.06.04 13:28:14.194 | PKV_DOR_B3_PKV-S-01_1 | Security Door (B3 WEST) | Unauthorised access | 2024.06.04 13:28:35.313 | sergio_paniagua |  | 0 | PKV | Door forced open without using a valid card
ACK Low | 2024.06.04 11:37:27.914 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown | 2024.06.04 13:17:38.644 | sergio_paniagua |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.06.04 11:37:27.914 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown | 2024.06.04 13:17:17.089 | sergio_paniagua |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.06.04 11:37:27.914 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown | 2024.06.04 13:18:35.962 | sergio_paniagua |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.06.04 10:25:25.629 | AEN-W-PSD-008 | Arden Platform 1 Zone 1 PSD 08 | PSD isolated | 2024.06.04 10:44:36.015 | kasturi_jathar |  | 0 | ARN | PSD isolated during a blockade
ACK Low | 2024.06.04 09:58:49.761 | PKV_DOR_B2_PKV-S-02_1 | Security Door (B2 EAST) | Unauthorised access | 2024.06.04 14:27:30.238 | sergio_paniagua |  | 0 | PKV | Door forced open without using a valid card
ACK Low | 2024.06.03 15:42:41.388 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Fire panels in the station have a fault | 2024.06.06 10:27:12.172 | himanshu_kakkad |  | 0 | AZC | Fire Panel Fault
ACK Low | 2024.06.03 10:47:25.309 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.06.03 10:47:25.307 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.06.03 10:47:25.302 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.06.03 10:47:25.298 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.06.03 10:03:20.712 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown | 2024.06.04 13:12:35.885 | sergio_paniagua |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.06.03 10:03:20.685 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown | 2024.06.04 13:12:35.911 | sergio_paniagua |  | 0 | SDU | CMS-ESS Interface not connected
ACK Low | 2024.06.03 10:03:13.526 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.06.03 12:33:52.544 | sergio_paniagua |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.06.03 10:03:13.400 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Door open too long | 2024.06.03 13:14:12.895 | sergio_paniagua |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.06.03 10:02:06.395 | AEN-SPE-0404 | B1, AEN-SPE-0404, 151-10 BOH Corridor | Heat or smoke detector fault | 2024.06.03 13:55:40.589 | kasturi_jathar |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:02:06.063 | AEN-SPE-0403 | B1, AEN-SPE-0403, 103-2 PAID CONC | Heat or smoke detector fault | 2024.06.03 13:55:38.503 | kasturi_jathar |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:02:05.448 | AEN-SPE-0400 | B1, AEN-SPE-0400, 103-2 PAID CONC | Heat or smoke detector fault | 2024.06.03 14:00:22.077 | kasturi_jathar |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:01:23.258 | AEN-SPE-0095 | B1, AEN-SPE-0095, 103-2 PAID CONC | Heat or smoke detector fault | 2024.06.03 14:00:24.072 | kasturi_jathar |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:01:22.348 | AEN-SPE-0090 | B1, AEN-SPE-0090, 151-10 BOH Corridor | Heat or smoke detector fault | 2024.06.03 14:00:25.761 | kasturi_jathar |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:01:17.713 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault | 2024.06.03 15:15:39.210 | emilio_ito |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.06.03 09:59:40.389 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator communications lost | 2024.06.03 14:21:42.497 | himanshu_kakkad |  | 0 | AZC | Escalators out of service
ACK Low | 2024.06.03 09:58:58.760 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy | 2024.06.04 13:16:15.141 | sergio_paniagua |  | 0 | AZC | General fault alarm as a result of loss of power
ACK Low | 2024.06.03 09:58:34.141 | PKV-W-PSD-004 | Parkville Platform 1 Zone 1 PSD 04 | PSD isolated | 2024.06.04 08:39:22.630 | sergio_paniagua |  | 0 | PKV | PSD isolated during a blockade
ACK Low | 2024.06.03 09:58:30.699 | PKV-E-PSD-027 | Parkville Platform 2 Zone 3 PSD 27 | PSD isolated | 2024.06.04 08:39:22.630 | sergio_paniagua |  | 0 | PKV | PSD isolated during a blockade
ACK Low | 2024.06.03 09:58:22.834 | AEN-E-PSD-022 | Arden Platform 2 Zone 3 PSD 22 | PSD isolated | 2024.06.03 14:00:37.428 | kasturi_jathar |  | 0 | ARN | PSD isolated during a blockade