## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.04.30 07:14:36.630 | PKV_TEP_0301_02_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | PKV
CAME UNACK Low | 2024.04.30 05:32:58.433 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.30 05:32:58.433 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.30 05:32:56.469 | PKV_LFT_0010 | Lift 10 BOH (B4 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK High | 2024.04.30 01:47:42.544 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK Med | 2024.04.30 01:47:42.544 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.30 01:46:08.567 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.04.30 01:15:49.550 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.04.30 01:15:49.550 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK Med | 2024.04.30 01:15:49.550 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.30 01:15:48.556 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Smoke detected in shaft! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.30 01:15:48.556 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.30 01:15:48.556 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Smoke detected in shaft! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.30 01:15:48.556 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.29 18:20:35.473 | PKV-Z-4352 | ZONE 4352: B2, PKV-AJ-01 Unallocated Area 299-5 | Confirmed fire! |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 17:30:09.496 | DMA_HWH_1001 | Hot Water Boiler | Communications lost alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:30:09.496 | DMA_HWH_1002 | Hot Water Boiler | Communications lost alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:49.583 | DMA_ESC_0007 | Escalator 7 Bank 5 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0002 | Escalator 2 Bank 2 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0003 | Escalator 3 Bank 3 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0008 | Escalator 8 Bank 6 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0009 | Escalator 9 Bank 6 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0010 | Escalator 10 Bank 6 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0011 | Escalator 11 Bank 7 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.579 | DMA_ESC_0012 | Escalator 12 Bank 7 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.569 | DMA_ESC_0001 | Escalator 1 Bank 1 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.569 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:49.569 | DMA_ESC_0005 | Escalator 5 Bank 3 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.04.29 17:28:44.699 | DMA_FCU_0109_MCV_01 | Fan Coil Unit - Chilled Water Valve | Analogue bad quality alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:44.699 | DMA_FCU_0109_MCV_01 | Fan Coil Unit - Chilled Water Valve | Modulated device position discrepancy fault alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:44.699 | DMA_FCU_0110_MCV_01 | Fan Coil Unit - Chilled Water Valve | Analogue bad quality alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:44.699 | DMA_FCU_0110_MCV_01 | Fan Coil Unit - Chilled Water Valve | Modulated device position discrepancy fault alarm |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:44.699 | DMA_FCU_0119_MVD_06 | Fan Coil Unit - Field Damper | Modulated device position discrepancy fault alarm |  |  |  | 0 | AZC
CAME UNACK Med | 2024.04.29 17:28:40.758 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Emergency Intercom Activated Level 2 |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 17:28:40.758 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 17:28:40.747 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 17:28:40.747 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 17:28:40.747 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 17:28:39.525 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 17:28:39.525 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 15:47:13.462 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 15:12:02.545 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 15:11:50.491 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 15:11:08.462 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 15:10:43.464 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 13:20:01.174 | _ReduManager | Distributed Server 1 | Server 1 - Preferred active |  |  |  | 0 | ARN | To be investigated
CAME UNACK Low | 2024.04.29 12:32:43.490 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 12:19:07.509 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.29 12:01:35.589 | DMA-SPE-0826 | B1, DMA-SPE-0826 Escalator 6 (B1 Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:35.536 | DMA-SPE-0806 | GF, DMA-SPE-0806 Escalator 6 (GF Pit) | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:32.599 | DMA-FPD-0008 | B1, DMA-FPD-0008 BOH CORRIDOR 151-12 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:32.599 | DMA-FPD-0009 | B1, DMA-FPD-0009 BOH CORRIDOR 151-12 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:32.599 | DMA-FPD-0010 | B1, DMA-FPD-0010 SCR 201-1 & ICR 211-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:32.599 | DMA-FPD-0011 | B1, DMA-FPD-0011 SCR 201-1 & ICR 211-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 12:01:29.632 | DMA-FLS-0006 | B1, DMA-FLS-0006 Sprinkler F/S | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 11:44:19.513 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Med | 2024.04.29 10:45:40.528 | _Mod_Plc_4_2 | MTPKV:_Mod_Plc_4_2. | ommunications Fault - Parkville Server 2 to Parkville EWIS |  |  |  | 0 | STL
CAME UNACK Low | 2024.04.29 10:10:03.511 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | AZC
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-0005 | GF, PKV-SPE-0005 Booster Cbd- ADJ S-5 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-0211 | B1, PKV-SPE-0211 LIFT 10 PKV-LFT-0010 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-1340 | GF, PKV-SPE-1340 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-1341 | GF, PKV-SPE-1341 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-1342 | GF, PKV-SPE-1342 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-1343 | GF, PKV-SPE-1343 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-SPE-1344 | GF, PKV-SPE-1344 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:34.042 | PKV-IVM-0055 | GF, PKV-IVM-0055 Booster Cupboard M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:39:33.997 | PKV-SPE-0027 | GF, PKV-SPE-0027 S-5 Fire Stair 1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:52.045 | PKV-SPE-0218 | B1, PKV-SPE-0218 NON HAB VOID 297-5 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.771 | PKV-IVM-0057 | GF, PKV-IVM-0057 Booster Cupboard M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.728 | PKV-IVM-0005 | B1, PKV-IVM-0005 S-02 Escape Stair 2 M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.728 | PKV-IVM-0030 | B1, PKV-IVM-0030 Station Hyd M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.728 | PKV-IVM-0031 | B1, PKV-IVM-0031 416-1 Hyd Tunnel M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.728 | PKV-IVM-0058 | GF, PKV-IVM-0058 Booster Cupboard M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.725 | PKV-IVM-0002 | B1, PKV-IVM-0002 S-02 Escape Stair 2 M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.725 | PKV-IVM-0003 | B1, PKV-IVM-0003 S-02 Escape Stair 2 M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.723 | PKV-FLS-0017 | B1, PKV-FLS-0017 BOH East F/Sw | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.723 | PKV-FLS-0018 | B1, PKV-FLS-0018 Hydrant Tunnel Met.F/Sw | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.723 | PKV-FLS-0019 | B1, PKV-FLS-0019 Hydrant Station Met.F/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:47.723 | PKV-IVM-0001 | B1, PKV-IVM-0001 S-02 Escape Stair 2 M/V | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1018 | B1 PKV-SPE-1018 FIRE INT LOBBY 403-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1019 | B1, PKV-SPE-1019 FIRE ESC CDOR 405-3 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1020 | B1, PKV-SPE-1020 FIRE ESC CDOR 405-3 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1320 | B1, PKV-SPE-1320 REFUSE COLLECT 238-18 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1321 | B1, PKV-SPE-1321 FIRE LOBBY 406-18 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-1339 | B1, PKV-SPE-1339 DRAIN PUMP ROOM 880-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-0021 | B1, PKV-SPE-0021 FIRE/GS LOBBY 402-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.483 | PKV-SPE-0927 | GF, PKV-SPE-0927 Control Cbd- ADJ S-5 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-0217 | B1, PKV-SPE-0217 GEN EXHAUST 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-0219 | B1, PKV-SPE-0219 DRAINAGE PUMP RM 880-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1000 | B1, PKV-SPE-1000 FIRE/GS LOBBY 402-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1008 | B1, PKV-SPE-1008 FIRE/GS LOBBY 402-2 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1009 | B1 PKV-SPE-1009 FIRE INT LOBBY 403-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1010 | B1 PKV-SPE-1010 FIRE INT LOBBY 403-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1011 | B1, PKV-SPE-1011 FIRE ESC CDOR 405-4 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1014 | B1, PKV-SPE-1014 FIRE LOBBY 406-3 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1015 | B1, PKV-SPE-1015 FIRE ESC. C'DOR 405-3 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.482 | PKV-SPE-1017 | B1, PKV-SPE-1017 FIRE ESC CDOR 405-3 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.481 | PKV-SPE-0170 | B1, PKV-SPE-0170 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.481 | PKV-SPE-0171 | B1, PKV-SPE-0171 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.481 | PKV-SPE-0214 | B1, PKV-SPE-0214 GEN EXHAUST 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.481 | PKV-SPE-0215 | B1, PKV-SPE-0215 GEN EXHAUST 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0014 | B1, PKV-SPE-0014 HVAC PLANT ROOM 811-4 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0101 | B1, PKV-SPE-0101 FIRE/GOODS LOBBY 402-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0102 | B1, PKV-SPE-0102 FIRE ESC. C'DOR 405-3 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0104 | B1, PKV-SPE-0104 FIRE ESC. C'DOR 405-4 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0105 | B1, PKV-SPE-0105 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0106 | B1, PKV-SPE-0106 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0120 | B1, PKV-SPE-0120 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0127 | B1, PKV-SPE-0127 REFUSE COLL.ROOM 238-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0129 | B1, PKV-SPE-0129 FIRE/GOODS LOBBY 402-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0130 | B1, PKV-SPE-0130 FIRE ESC. C'DOR 405-3 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0131 | B1, PKV-SPE-0131 FIRE LOBBY 406-3 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.070 | PKV-SPE-0168 | B1, PKV-SPE-0168 FIRE ESC. C'DOR 405-3 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.069 | PKV-SPE-0003 | B1, PKV-SPE-0003 FIRE/GOODS LOBBY 402-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:46.069 | PKV-SPE-0006 | GF, PKV-SPE-0006 Control Cbd- ADJ S-5 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0126 | B1, PKV-SPE-0126 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0128 | B1, PKV-SPE-0128 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0137 | B1, PKV-SPE-0137 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0141 | B1, PKV-SPE-0141 GEN. EXH SHAFT 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0172 | B1, PKV-SPE-0172 FIRE INT. LOBBY 403-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0181 | B1, PKV-SPE-0181 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0182 | B1, PKV-SPE-0182 FIRE LOBBY 406-14 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0183 | B1, PKV-SPE-0183 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0188 | B1, PKV-SPE-0188 GEN. EXH SHAFT 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0203 | B1, PKV-SPE-0203 GEN. EXH SHAFT 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0204 | B1, PKV-SPE-0204 GEN. EXH SHAFT 823-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0208 | B1, PKV-SPE-0208 ECS O/A SHAFT 820-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0209 | B1, PKV-SPE-0209 ECS O/A SHAFT 820-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-0210 | B1, PKV-SPE-0210 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1001 | B1, PKV-SPE-1001 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1002 | B1, PKV-SPE-1002 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1003 | B1, PKV-SPE-1003 FIRE LOBBY 406-14 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1004 | B1, PKV-SPE-1004 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1005 | B1, PKV-SPE-1005 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1006 | B1 PKV-SPE-1006 FIRE INT LOBBY 403-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1007 | B1 PKV-SPE-1007 FIRE INT LOBBY 403-1 C/S | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1012 | B1, PKV-SPE-1012 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.973 | PKV-SPE-1013 | B1, PKV-SPE-1013 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:44.972 | PKV-SPE-0125 | B1, PKV-SPE-0125 FIRE ESC. C'DOR 405-2 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:42.017 | PKV-SPE-0016 | B1, PKV-SPE-0016 Mech Riser 821-6 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:42.017 | PKV-SPE-0017 | B1, PKV-SPE-0017 WATER METER ROOM 884-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:42.017 | PKV-SPE-0018 | B1, PKV-SPE-0018 Gas Meter Room 944-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:42.017 | PKV-SPE-0213 | B1, PKV-SPE-0213 FIRE ESC. C'DOR 405-4 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:42.017 | PKV-SPE-0020 | B1, PKV-SPE-0020 BOH CORRIDOR 884-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:39.977 | PKV-SPE-0103 | B1, PKV-SPE-0103 SPRINKLER RISER 416-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:38:31.985 | PKV-SPE-0013 | GF, PKV-SPE-0013 LIFT 11 PKV-LFT-0011 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 09:11:11.189 | AEN_DOR_B2_ESC_STAIRS_04_3 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.04.29 08:43:51.364 | AEN_DOR_B1_151-3_1 | West BOH Corridor Entry - Concourse | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.04.29 08:24:13.310 | DMA-FPD-0016 | B1, DMA-FPD-0016 ECS PLANTROOM 3 802-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 08:24:13.309 | DMA-FPD-0015 | B1, DMA-FPD-0015 ECS PLANTROOM 3 801-5 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 08:24:13.307 | DMA-FPD-0014 | B1, DMA-FPD-0014 ECS PLANTROOM 3 802-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 08:24:13.296 | DMA-FPD-0004 | B1, DMA-FPD-0004 OAF-1102 Plant Rm 801-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.04.29 08:24:13.295 | DMA-FPD-0003 | B1, DMA-FPD-0003 OAF-1101 Plant Rm 801-3 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Med | 2024.04.29 08:24:13.253 | DMA-FIP-0006 | Anzac Station SHCIE Panel 6 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Med | 2024.04.29 08:24:13.251 | DMA-FIP-0005 | Anzac Station SHCIE Panel 5 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Med | 2024.04.29 08:24:13.039 | DMA-FIP-0004 | Anzac Station SHCIE Panel 4 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Med | 2024.04.29 08:24:13.034 | DMA-FIP-0003 | Anzac Station SHCIE Panel 3 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Med | 2024.04.29 08:24:13.031 | DMA-FIP-0002 | Anzac Station SHCIE Panel 2 | Power supply to gas supression panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Med | 2024.04.29 08:24:13.028 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Power supply to fire panel fault |  |  |  | 0 | AZC | Loss of Power
CAME UNACK Low | 2024.04.29 08:09:20.158 | AEN_DOR_B2_ESC_STAIRS_03_2 | Security Door (B2 WEST) | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.04.29 01:50:23.703 | AEN-FLS-0008 | GF, AEN-FLS-0008, SCV1-RETAIL 1 Spr.F/S | Heat or smoke detector fault |  |  |  | 0 | ARN | To be investigated
CAME UNACK Low | 2024.04.28 19:33:51.133 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK High | 2024.04.26 17:05:27.613 | PKV_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Smoke detected in shaft! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.26 17:05:27.613 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Smoke detected in shaft! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.04.26 17:05:27.613 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK Low | 2024.04.26 14:47:01.740 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.26 09:47:59.239 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.04.24 21:35:36.071 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.24 21:35:36.071 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.24 21:32:33.122 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:31:09.243 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:30:05.156 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:26:25.113 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:23:05.137 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:19:29.229 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:17:43.117 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:15:07.215 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.24 21:15:07.215 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.24 21:08:05.152 | PKV_ESC_0007 | Escalator 7 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:07:02.062 | PKV_ESC_0008 | Escalator 8 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:05:59.230 | PKV_ESC_0009 | Escalator 9 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 21:00:57.124 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 20:59:35.112 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK High | 2024.04.24 13:45:33.135 | TSC-E-PED-001 | Town Hall Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
ACK Low | 2024.04.24 13:33:37.955 | AEN_ESC_0007 | Escalator 7 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.04.26 12:31:55.442 | dominic_dlasselle |  | 0 | ARN | Escalators out of service
CAME UNACK Low | 2024.04.24 13:26:54.932 | AEN_ESC_0006 | Escalator 6 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | ARN | Escalators out of service
CAME UNACK Low | 2024.04.24 12:59:18.935 | AEN_ESC_0005 | Escalator 5 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | ARN | Escalators out of service
CAME UNACK Low | 2024.04.24 12:43:02.144 | AEN_DOR_B1_ESC_STAIRS_03_1 | West Emergency Stairs - Concourse | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK High | 2024.04.24 11:00:43.130 | DMA-E-PED-001 | Anzac Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK Low | 2024.04.24 10:46:36.599 | AEN_DOR_B1_151-4_1 | Security Door (B1 EAST) | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK High | 2024.04.24 10:41:09.127 | DMA-E-PED-002 | Anzac Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK Med | 2024.04.24 10:38:45.141 | TSC-E-PSD-027 | Town Hall Platform 2 Zone 3 PSD 27 | Low motor current |  |  |  | 0 | THL
CAME UNACK Low | 2024.04.24 10:38:45.139 | TSC-E-PSD-018 | Town Hall Platform 2 Zone 2 PSD 18 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK High | 2024.04.24 10:27:57.133 | DMA-W-PED-001 | Anzac Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | AZC | PED Opening
CAME UNACK Low | 2024.04.24 09:21:49.207 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.24 09:21:49.207 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.04.23 12:48:58.186 | SYP-DT-1011 | Eastbound zone 2 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.23 12:29:52.241 | AEN_DOR_B1_ESC_STAIRS_03_2 | West Emergency Stairs - Concourse | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.04.22 14:14:56.187 | SYP-DT-1009 | Eastbound zone 1 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 14:14:56.187 | SYP-DT-1012 | Eastbound zone 2 sonar sensor 2 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 13:44:42.301 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.301 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.301 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.301 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.301 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.300 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 13:44:42.298 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 12:22:46.188 | SYP-DT-1013 | Westbound zone 1 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK High | 2024.04.22 12:12:39.168 | SYP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU
CAME UNACK High | 2024.04.22 10:12:18.564 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.04.22 10:12:18.564 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.22 10:11:54.564 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.22 09:02:53.065 | AEN-W-PED-002 | Arden Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.04.22 09:02:52.782 | AEN-E-PED-002 | Arden Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK Low | 2024.04.22 09:02:31.880 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift is not Operational |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.04.22 09:02:28.865 | AEN-FIP-0001 | Arden Main Fire Panel | Fire panels in the station have a fault | 2024.04.22 09:48:59.644 | operator |  | 0 | ARN | Isolation of panel
CAME UNACK Med | 2024.04.22 08:57:30.529 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.04.22 08:57:30.340 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.04.22 08:57:29.401 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.04.22 08:55:12.810 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:55:11.935 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.04.22 08:55:11.381 | AEN-E-PED-001 | Arden Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK Low | 2024.04.22 08:55:09.712 | SKP-DT-1008 | Westbound zone 2 sonar sensor 2 | Train detection sensor fault |  |  |  | 0 | SDU | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.04.22 08:55:09.692 | SKP-DT-1007 | Westbound zone 2 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.672 | SKP-DT-1006 | Westbound zone 1 sonar sensor 2 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.653 | SKP-DT-1005 | Westbound zone 1 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.633 | SKP-DT-1004 | Eastbound zone 2 sonar sensor 2 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.614 | SKP-DT-1003 | Eastbound zone 2 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.594 | SKP-DT-1002 | Eastbound zone 1 sonar sensor 2 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:09.574 | SKP-DT-1001 | Eastbound zone 1 sonar sensor 1 | Train detection sensor fault |  |  |  | 0 | SDU
CAME UNACK High | 2024.04.22 08:55:08.153 | SKP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU
CAME UNACK High | 2024.04.22 08:55:08.128 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:06.728 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 08:55:06.709 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 08:55:06.676 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 08:55:06.646 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 08:55:06.626 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.04.22 08:55:06.605 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Med | 2024.04.22 08:55:05.225 | SKP-PLC-0001 | South Kensington PLC | PLC system fault |  |  |  | 0 | SDU
CAME UNACK Low | 2024.04.22 08:55:00.765 | PKV_DOR_B4_PKV-S-02_3 | Security Door (B4 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.04.22 08:55:00.761 | PKV_DOR_B4_PKV-S-02_2 | Security Door (B4 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.04.22 08:55:00.727 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.04.22 08:55:00.717 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
ACK Low | 2024.04.22 08:55:00.670 | AEN_DOR_GF_246-1_1 | Security Door (GF WEST) | Unauthorised access | 2024.04.24 09:10:00.791 | kai_longley |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.04.22 08:55:00.659 | AEN_DOR_B2_ESC_STAIRS_04_3 | Security Door (B2 EAST) | Door open too long | 2024.04.24 09:10:41.323 | kai_longley |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK High | 2024.04.22 08:52:51.751 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.04.22 08:52:51.741 | TNC-E-PED-002 | State Library Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK Low | 2024.04.22 08:51:36.167 | AEN-W-PSD-015 | Arden Platform 1 Zone 2 PSD 15 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK High | 2024.04.22 08:51:21.535 | AEN-W-PSD-009 | Arden Platform 1 Zone 1 PSD 09 | PSD Unscheduled Door Opening! |  |  |  | 0 | ARN | PSD Opening
CAME UNACK Low | 2024.04.22 08:51:20.143 | AEN-W-PSD-009 | Arden Platform 1 Zone 1 PSD 09 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:51:17.419 | AEN-W-PSD-008 | Arden Platform 1 Zone 1 PSD 08 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:51:14.710 | AEN-W-PSD-007 | Arden Platform 1 Zone 1 PSD 07 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:51:01.466 | AEN-W-PSD-002 | Arden Platform 1 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK High | 2024.04.22 08:50:39.083 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD Unscheduled Door Opening! |  |  |  | 0 | ARN | PSD Opening
CAME UNACK Low | 2024.04.22 08:50:37.711 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:50:24.478 | AEN-E-PSD-018 | Arden Platform 2 Zone 2 PSD 18 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:50:16.535 | AEN-E-PSD-015 | Arden Platform 2 Zone 2 PSD 15 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK High | 2024.04.22 08:50:00.849 | TNC-W-PED-001 | State Library Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.04.22 08:50:00.837 | TNC-E-PED-001 | State Library Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK Med | 2024.04.22 08:49:21.229 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.04.22 08:49:21.226 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:48:57.840 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:48:57.293 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Low | 2024.04.22 08:48:54.891 | TSC-E-PSD-020 | Town Hall Platform 2 Zone 2 PSD 20 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:48:46.490 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:48:41.480 | TSC-E-PSD-004 | Town Hall Platform 2 Zone 1 PSD 04 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:48:40.616 | TSC-E-PSD-003 | Town Hall Platform 2 Zone 1 PSD 03 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:48:39.761 | TSC-E-PSD-002 | Town Hall Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.04.22 08:48:38.892 | TSC-E-PSD-001 | Town Hall Platform 2 Zone 1 PSD 01 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK High | 2024.04.22 08:48:22.518 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:48:21.913 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:48:21.658 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.04.22 08:48:05.490 | AEN-W-EED-001 | Arden Platform 1 Zone 1 EED 01 | EED Unscheduled Door Opening! |  |  |  | 0 | ARN | EED Opening
ACK Med | 2024.03.25 10:37:49.805 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.803 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.802 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.799 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.798 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.796 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.795 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.03.25 10:37:49.793 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.03.25 15:58:37.659 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
CAME UNACK Low | 2024.03.25 10:37:49.767 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 |  |  |  | 0 | THL
ACK Low | 2024.03.25 10:37:49.764 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.04.11 09:41:56.762 | kai_longley |  | 0 | ARN | To be investigated
CAME UNACK Med | 2024.03.25 10:37:49.760 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost |  |  |  | 0 | THL
CAME UNACK Low | 2024.03.25 10:37:49.756 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 |  |  |  | 0 | THL
ACK Low | 2024.03.25 10:37:49.754 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.04.11 09:41:56.762 | kai_longley |  | 0 | ARN | To be investigated
ACK Med | 2024.03.25 10:37:49.745 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.04.11 09:41:56.762 | kai_longley |  | 0 | ARN | To be investigated
ACK Med | 2024.03.08 12:02:27.852 | _RDBArchive_2 | Anzac Server 2 | RDB Connection Lost | 2024.04.11 09:41:56.763 | kai_longley |  | 0 | ARN | To be investigated
CAME UNACK Med | 2024.03.08 12:02:27.845 | _RDBArchive | Anzac Server 1 | RDB Connection Lost |  |  |  | 0 | AZC
ACK Med | 2023.10.10 08:29:54.232 | _RDBArchive_2 | Town Hall Server 2 | RDB Connection Lost | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | To be investigated
ACK Med | 2023.10.10 08:29:54.231 | _RDBArchive | Town Hall Server 1 | RDB Connection Lost | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | THL | To be investigated
ACK Med | 2023.10.10 08:29:53.877 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC
ACK Med | 2023.10.10 08:29:53.243 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC
ACK Med | 2023.10.10 08:29:52.927 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | THL
ACK Med | 2023.10.10 08:29:50.304 | _Mod_Plc_4_2 | MTTHL:_Mod_Plc_4_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC
ACK Med | 2023.10.10 08:29:49.671 | _Mod_Plc_3_2 | MTTHL:_Mod_Plc_3_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC
ACK Med | 2023.10.10 08:29:49.030 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC
ACK Med | 2023.10.10 08:12:51.271 | _RDBArchive_2 | State Library Server 2 | RDB Connection Lost | 2023.11.28 08:35:41.432 | chris_lawson |  | 0 | THL
ACK Med | 2023.10.10 08:12:51.268 | _RDBArchive | State Library Server 1 | RDB Connection Lost | 2023.11.28 08:35:41.432 | chris_lawson |  | 0 | STL