## CMS_SAC Test
Colour Legned
Okay and passed
Not okay due to issue / Need 's re-testing
S.NO | Asset ID | Device Description (CMS Use) | Type | Unlock command | Lock/Unlock status | Open/Close status | DOTL | Unauthorised Event by exception | Test Date | Test Status (T&C) | 19/04/2024 Test Comments | Test Comments (T&C) | Delivery comments (Heap) | Forcefeild comments (Scott) | CMS Comments (Eric / Luke) | Action / Next Step | CYP DEFECT | Unauthorised Event by exception
30 | AEN_ROL_GF_102-1_2 | Main Entrance Roller Door - Ground Floor | ROL | N/A | N/A | ok | [5 empty] | 18/04/2024 - Both roller doors are operned by the open and close signals sent by the CMS and there are no unexpected alarms for the roller doors when they are being used | 09/02/24 - Not in SAC's design |  | 5/02/24 Roller door (above myki) added 9/02/24 Wiring issues so currently the door can not be added to CMS | Retest once the door is ready in CMS
7 | AEN_ROL_GF_102-1_1 | Bypass Roller Door - Ground Floor | ROL | N/A | N/A | ok | N/A |  | 2024-02-20 | Passed |  | Open command successful, close command ok swipe card working ok Note: Swipe card not linked to UDO | 09/02/24: Description incorrect, SAC's design is for the bypass gate/roller door, Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | 1/2/24 Open and Closed commands tested OK. Input event for Unauthorised Access also tested but DPT doesn't yet have alarm configured 20/2/24 All OK. NOTE: Unauthorised Access alarm triggers when area is secure even when using the swipe card | Complete |  | Ok
12 | AEN_DOR_LG_ESC_STAIR_07_1 | West Emergency Stairs - Lower Ground Floor | CON | OK | OK | OK |  | OK | 1/02/2024 26/03/2024 04/04/2024 10/04/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds NO DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds NO DOTL. No UDO. Unauthorised access - Door Open without swipe.UDO PRESENT | 1. Open and Close status and DOTL is not working. 2. This door has a faulty electronic mortice lock ,it has been entered into OmTrak and CYP are aware as per chrisitian Heap's email. With CYP 24/1 26 Mar 2024: Non-NAC door. Design limitation for implementing UDO/Forced door open alarm in forcefield acc. to Scott. 04 Apr 2024: UDO is ok. However, the DOTL alarm is still present. When the card is swiped and door is open for long, DOTL alarm appears along with UDO. When the card is not swiped, UDO appears when the door is opened, and DOTL appears when the door is kept open for long. 10 Apr 2024 : UDO alarms works Note: When door is opened from inside (where there is no swipe card reader) UDO alarm appears. Since this is plant maintenace room the UDO is not excepted when opened from inside . This case is applicable for all CON doors with card reader on one side. RNA design issue. |  |  | Panel 604 Door 34 1/02/2024 Non NAC door 20/2/24 All OK | Complete |  | Ok
24 | AEN_DOR_LG_405-3_2 | Fire escape Corridor - Lower Ground Floor | CON | OK | OK | OK |  | Unable to test Today | 2024-02-20 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key | 31/01 -test from 1-Feb Could not find support to power off magnetic lock to test UDO (unplanned test) Require OCS team to test UDO. | 09/02/24 : Testers need to procure break glass testing keys so they can de-energise the mag locks to simulet forced doors -no need for delivery interface |  | Panel 607 Door 21 20/2/24 All OK | Complete |  | Ok
25 | AEN_DOR_LG_405-3_1 | Fire escape Corridor - Lower Ground Floor | CON | OK | OK | OK |  |  | 2024-02-20 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key | 31/01 -test from 1-Feb Could not find support to power off magnetic lock to test UDO (unplanned test) Require OCS team to test UDO. | 09/02/24 : Testers need to procure break glass testing keys so they can de-energise the mag locks to simulet forced doors -no need for delivery interface |  | Panel 607 Door 22 20/2/24 All OK | Complete |  | Ok
11 | AEN_DOR_L2_ESC_STAIRS_5_2 | East Emergency Stairs - Level 2 | CON | OK | OK | OK |  | Unable to test Today | 23/01/2024 29/02/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. When door is closed the alarm clears. Unauthorised access - Door Open without swipe. No UDO present. PUSH BAR USED | 1. When door is unlocked + opened and locks automatically . The unlocked status doesn't change to locked. 2. When the door is unlocked from locked+closed position, the door status changed to "unlocked" but once the door locks automatically the status changed to "locked" after about 1 min. 3. CMS Icon Issue - icon displays locked symbol when door is closed & Unlocked, and displays unlocked symbol when door is Opened & Locked. (After unlocking, the lock engages automatically after 5 sec. i.e. Unlock -> Open Door -> Lock engaged.) |  |  | 23/1/24 Secure/Locked event also took a minute to come through on Forcefield server. Shunt time changed to 30 seconds to speed up the event | Complete |  | Ok
10 | AEN_DOR_L1_ESC_STAIRS_5_1 | East Emergency Stairs - Level 1 | CON | OK | OK | OK |  | OK | 16/01/2024 29/02/2024 26/03/2024 04/04/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds no DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds NO DOTL. No UDO. When door is closed the alarm clears. Unauthorised access - Door Open without swipe. UDO present No unauthorised access or DOTL when the door is held open for more than 30 seconds. Waited a minute. tested 3 times at 0952 | 1. CMS Icon Issue - icon displays locked symbol when door is closed & Unlocked, and displays unlocked symbol when door is Opened & Locked. (After unlocking, the lock engages automatically after 5 sec. i.e. Unlock -> Open Door -> Lock engaged.) 26 Mar 2024: Non-NAC door. Design limitation for implementing UDO/Forced door open alarm in forcefield acc. to Scott. 04 Apr 2024: UDO is ok. Non-CMS Issue - Door is not unlocking when card is swiped (card reader beeps continously when swiped). 18/04/24: Door retested - Command works, card reader opens door. UDO appears when the door is open for more than 30 seconds. When door is held open the open signal on the door stays true. |  |  | Panel 601 Door 18 Non-NAC door 20/2/24 All OK | Complete |  | Ok
8 | AEN_DOR_GF_ESC_STAIR_9_1 | After hours access - Ground Floor | CON | OK | OK | OK |  | Unable to test today | 2024-01-23 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. When door is closed the alarm clears. Unauthorised access - Door Open without swipe. No UDO present. PUSH BAR USED | 1. When the door is unlocked from locked+closed position, the door status changed to "unlocked" but once the door locks automatically the status changed to "locked" after about 1 min. 2. When door is unlocked + opened and locks automatically . The unlocked status doesn't change to locked. 3. Open and Close status is not working. 4. If door is open long enough to trigger DOTL, when closing the door the CMS status will go straight to locked status. 5. To be retested once CMS configuration for double door is updated. |  |  | 18/1/24 Double door. Locked event takes a minute to come through 23/1/24 Mechanical arm prevents the primary door from closing if secondary door is open Locked/secure event takes 30 seconds as per shunt time | Complete |  | Ok
23 | AEN_DOR_GF_405-2_2 | East Emergency Stairs - Ground Floor | CON | OK | OK | OK |  | OK | 1/02/2024 29/02/2024 26/03/2024 04/04/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds no DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds NO DOTL. No UDO. When door is closed the alarm clears. Unauthorised access - Door Open without swipe. UDO present No unauthorised access or DOTL when the door is held open for more than 30 seconds. Waited a minute. tested 3 times at 0954 | 31/01 -test from 1-Feb 26 Mar 2024: Non-NAC door. Design limitation for implementing UDO/Forced door open alarm in forcefield acc. to Scott. |  |  | Panel 601 Door 30 1/2/24 Non NAC door so unauthorised event not possible 20/2/24 All OK | Complete |  | Ok
7 | AEN_DOR_GF_405-2_1 | Fire Escape Corridor - Ground Floor | CON | OK | OK | OK |  | OK | 23/01/2024 26/03/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, no alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. UDO present. | 1. Open and Close status is not working . May be due to open wiring at the door. 2. When door is unlocked + opened and locks automatically . The unlocked status doesn't change to locked. 3. When the door is unlocked from locked+closed position, the door status changed to "unlocked" but once the door locks automatically the status changed to "locked" after about 1 min. 3.1 If door is open long enough to trigger DOTL, when closing the door the CMS status will go straight to locked status. 4. CMS Icon Issue - icon displays locked symbol when door is closed & Unlocked, and displays unlocked symbol when door is Opened & Locked. (After unlocking, the lock engages automatically after 5 sec. i.e. Unlock -> Open Door -> Lock engaged.) | RSW not finished / handed to delivery - testing in new year |  | 18/1/24 Locked event takes a minute to come through. 23/1/24 Locked/secure event takes 30 seconds as per shunt time Mechanical arm prevents the primary door from closing if secondary door is open | Complete |  | Ok
6 | AEN_DOR_GF_401-1_1 | Fire Control Room Entry - Ground Floor | CON | OK | OK | OK |  | OK | 23/01/2024 26/03/2024 04/04/2024 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds NO DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds NO DOTL. No UDO. Unauthorised access - Door Open without swipe. UDO present. | 1. When the door is unlock + Open with swipe card the Physically the door lock is not working. 2. Open and Close status is not working. 3. Unlock command not working. 26 Mar 2024: Non-NAC door. Design limitation for implementing UDO/Forced door open alarm in forcefield acc. to Scott. | Door not marked as finished by CYP, nothing tested, STW or commissioned [SS] 17/01 - waiting for CYP to repair - Need date from George 25/01/24 - Door tested and operational, except for Key Over-ride, should not delay CMS testing |  | 18/1/24 Events not coming through. Unlock command not working. Door not ready 23/1/24 Locked/secure DOESN'T take 30 seconds to come through. Door not connected to NAC, so Unauthorised event not possible. 20/2/24 All OK | Complete |  | Ok
5 | AEN_DOR_GF_246-2_2 | East Loading Bay Entry - Ground Floor | CON | OK | OK | OK |  |  | 2024-01-23 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key Door requires pressure to close properly. CANNOT CLOSE FROM INSIDE PUSH BUTTON TESTED NO UDO | 1. Swipe card reader is not working. LED's of card reader is off . looks like the Reedswitch is not powdered on. 2. When unlock command is issued status changed to unlock , but physically the lock or unlock not working as there is no power. 3. When door is unlocked + opened and locks automatically . The unlocked status doesn't change to locked. 4. When the door is unlocked from locked+closed position, the door status changed to "unlocked" but once the door locks automatically the status changed to "locked" after about 1 min. 5. CMS device icon displays only open status on both door open and close. 6. Open / Close status discrepeny when secondary leaf is open and primary leaf is closed. (CMS displays closed status instead of open). 7. To be retested once CMS configuration for double door is updated. Non CMS issue : 1.Door doesn't close by itself. CYP defect | Door not marked as finished by CYP, nothing tested, STW or commissioned [SS] 17/01 - waiting for CYP to repair - Need date from George |  | 18/1/24 Double door. Events coming through but not correctly. Open / closed is off a single door not both. 23/1/24 Locked/secure event takes 30 seconds as per shunt time. Door shows as closed if the leaf without the lock is left open Unauthorised access tested by cutting power to the mag lock Door doesn't close by itself. CYP defect | Complete |  | Ok
4 | AEN_DOR_GF_246-2_1 | East Loading Bay Entry - Ground Floor | CON | OK | OK | OK |  | Unable to test Today | 2024-01-23 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key Door requires pressure to close properly. CANNOT CLOSE FROM INSIDE PUSH BUTTON TESTED NO UDO | 1. Swipe card reader is not working. LED's of card reader is off . looks like the Reedswitch is not powdered on. 2. CMS device icon displays only open status on both door open and close. 3. DOTL not working. Appears randomly and clears after remote unlock command. 4. Open / Close status discrepeny when secondary leaf is open and primary leaf is closed. (CMS displays closed status instead of open). 5. To be retested once CMS configuration for double door is updated. Non CMS issue : 1.Door opens by itself when unlocked. Door doesn't close by itself. CYP defect | Door not marked as finished by CYP, nothing tested, STW or commissioned [SS] 17/01 - waiting for CYP to repair - Need date from George |  | 18/1/24 Events not coming through. Wiring not complete. 23/1/24 Locked/secure event takes 30 seconds as per shunt time. Door shows as closed if the leaf without the lock is left open Door opens by itself when unlocked. Door doesn't close by itself. CYP defect | Complete |  | Ok
3 | AEN_DOR_GF_246-1_2 | West Loading Bay Entry - Ground Floor | CON | OK | OK | OK |  | OK | 2024-01-23 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key Door requires pressure to close properly. CANNOT CLOSE FROM INSIDE PUSH BUTTON TESTED NO UDO | 1. Swipe card is indicating fault . Red LED is displayed. 2. Unlock / lock status not working. 3. DOTL not working. Appears randomly and clears only after unlock command is issued. 4. Open/ close status not working even when second door is opened. 5. To be retested once CMS configuration for double door is updated. | Door not marked as finished by CYP, nothing tested, STW or commissioned [SS] 17/01 - waiting for CYP to repair - Need date from George |  | 23/1/24 Locked/secure event takes 30 seconds as per shunt time. Door has mechanical inhibit to close primary door when secondary door is open | Complete |  | Ok
2 | AEN_DOR_GF_246-1_1 | West Loading Bay Entry - Ground Floor | CON | OK | OK | OK |  | OK | 2024-01-23 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key Door requires pressure to close properly. CANNOT CLOSE FROM INSIDE PUSH BUTTON TESTED NO UDO | 1. Swipe card is indicating fault . Red LED is displayed. 2. Unlock / lock status not working. 3. DOTL not working. Appears randomly and clears only after unlock command is issued. 4. When the first door is open or closed , open / close status didnt change . But when the second door is opened or closed the status changes to open / close. 5. To be retested once CMS configuration for double door is updated. | Door not marked as finished by CYP, nothing tested, STW or commissioned [SS] 17/01 - waiting for CYP to repair - Need date from George |  | 23/1/24 Locked/secure event takes 30 seconds as per shunt time. Door has mechanical inhibit to close primary door when secondary door is open | Complete |  | Ok
9 | AEN_DOR_GF_151-12_1 | Access to office - Ground Floor | CON | OK | OK | OK |  | Unable to test Today | 2024-01-25 | Passed | 19/04/24 - Remote control - Unlock command opened door, No alarm. After 30 seconds DOTL Alarm appears. No UDO appeared. After door shut alarms clear Local Control - Swipe card unlocked door with no alarm. After 30 seconds DOTL. No UDO. Unauthorised access - Door Open without swipe. NO UDO present. could not test without key Could not test UDO today | 1. Open wiring exisit at the door. 2. CMS not receiving open / close / unlocked / locked status . 3. Unlock command is received by the card reader but not by the physical lock. 4. Unauthorised access event to be tested. Christian team is required to test. (Power Off) 5. To be retested once CMS configuration for double door is updated. Non CMS issue : 1.Mechanical arm present but doesn't work. CYP defect | Previously tested and working - CYP removed maglock without notifying RNA - will be added to OmTrak |  | 18/1/24 Double door. Unlock beeps on swipe card but no lock sound. Events looked to be coming through yesterday but nothing coming through today 23/1/24 Mechanical arm present but doesn't work. CYP defect Locked/secure event takes 30 seconds as per shunt time Couldn't test the unauthorised event as the power to the mag lock needs to be cut 25/1/24 Tested the forced event by powering off the mag lock 1/2/24 Forcefield can't be configured to deal with double door statuses. It only uses the primary leaf read switch. | Complete |  | Ok
20 | AEN_DOR_B2_ESC_STAIRS_04_4 | East Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 23/01/2024 29/02/2024 26/03/2024 | Passed |  | 1. Physically the door can't be opened using swipe card on one side and can be opened by push bar on other side of the door. 2. Open and close status is not working. 3. DOTL not working 4. Door opened using push bar without swipping the card , but unauthorised event doesn't come through.Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure 16-Feb-2024: UDO - Card reader events not coming through from forcefield. Scott to check 20-Feb-2024: Scott is not able to access Card Reader CRD 1108 (Christian to contact Scott) 29-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 18/04/2024 - Retested door is working as expected | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 602 Door ?? 23/1/24 Unauthorised event yet to be configured in Forcefield. DOTL added as an Input event 16/2/24 Forcefield not sending door events 20/2/24 Not Door 22 in Forcefield - Scott needs to configure but having issues - unable to access NAC that the door is on | Complete |  | Ok
21 | AEN_DOR_B2_ESC_STAIRS_04_3 | East Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 29/02/2024 26/03/2024 | Passed |  | 1.. Physically door is not locked . We can open from either side without unlocking. 2. From swipe card lock/ unlock status not working. CMS always displays as locked status. 3. When the first door is open or closed , open / close status didnt change . But when the second door is opened or closed the status changes to open / close. 4. Door opened using push bar without swipping the card , but unauthorised event doesn't come through.With RNA Design & Scott to reconfigure 5. No DOTL alarm 16-Feb-2024: UDO - Card reader events not coming through from forcefield. Scott to check 20-Feb-2024: Scott is not able to access Card Reader 1109 (Christian to contact Scott) 29-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 18/04/24 Door retested - Door is remaining in the Open state and there is no UDO appearing for the door. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 602 Door ?? 23/1/24 Double door. Closed when one leaf open. CMS to be updated to monitor both read switches 1/2/24 DOTL fixed on Forcefield and address updated in CMS 16/2/24 Forcefield not sending door events 20/2/24 Not Door 21 in Forcefield - Scott needs to configure but having issues - unable to access NAC that the door is on | Complete |  | Ok
16 | AEN_DOR_B2_ESC_STAIRS_04_2 | East Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 20/02/2024 29/02/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. DOTL not working 2.CMS Icon Issue - icon displays locked symbol when door is closed & Unlocked, and displays unlocked symbol when door is Opened & Locked. (After unlocking, the lock engages automatically after 5 sec. i.e. Unlock -> Open Door -> Lock engaged.) 3. Door opened using push bar without swipping the card , but unauthorised event doesn't come through.Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure 4.Open and close status is not working. 16-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04-Apr-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 18/04/24 Retested - Door operated as expected. When the door is held open the UDO goes active and the Open status remains true. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 605 Door 22 23/1/24 Had to add DOTL input event 13. Unautorised event not yet configured 16/2/24 DOTL not working. Unauthorised working with CMS script 20/2/24 All OK (DOTL Input 013 not 13) | Complete |  | Ok*
13 | AEN_DOR_B2_ESC_STAIRS_04_1 | East Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 29/02/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. Swipe card is indicating fault . Red LED is displayed. 2.From swipe card lock/ unlock status not working. CMS always displays as locked status. 3.Door opened using push bar without swipping the card , but unauthorised event doesn't come through.Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure 20-Feb-2024: UDO - CRD1106 Card reader events not coming through from forcefield. Card reader has fault (Red LED). Card reader require reconfiguration according to Scott. Christian to check 29-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04-Apr-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 18/04/24 Door retested and working as expected. When the door is held open a UDO appears and the state of the door remains open | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 605 Door 21 23/1/24 Had to add DOTL input event 12. Unautorised event not yet configured 16/2/24 Card reader events not coming - not even beeping - red light 20/2/24 (DOTL Input 012 not 12) Carder reader fault | Complete |  | Ok*
17 | AEN_DOR_B2_ESC_STAIRS_03_2 | West Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 29/02/2024 26/03/2024 | Passed | Open/Close - Swipe card open no alarm, after holding open for 30 seconds NO UDO alarm Unauthorised Access - Push bar access caused UDO | 1. Swipe card reader not installed. So lock/unlock cann't be tested. With CYP to rectify, faulty cable ETA TBC, unlikely to be quick 2. Open and close status is not working. 3. DOTL not working 4. Door opened using push bar without swipping the card , but unauthorised event doesn't come through.With RNA Design & Scott to reconfigure 5. 16-Feb-2024: Wall cladding is missing and Swipe card reader (CRD 1123) is not installed - will be required to test Unauthorized alarm 26-Mar-2024: Tested with temporary card reader since wall cladding is not yet installed. 18/04/24 Retested Card reader unavailable. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | 23/1/24 Double door. Closed when one leaf open. CMS to be updated to monitor both read switches 1/2/24 DOTL fixed on Forcefield and address updated in CMS | Complete |  | Not ok
19 | AEN_DOR_B2_ESC_STAIRS_03_1 | West Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 23/01/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. Physically the door can't be opened when unlocked using swipe card. 2. Lock / unlock status is received just taping on swipe card. 3. Open and close status is not working. 4. DOTL not working. 5.Door opened using push bar without swipping the card , but unauthorised event doesn't come through.Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure. 31/1 - Unknown status, check in with PB & Design, James Conheady 16-Feb-2024: UDO - Forcefield only sends entry event and not the Secure/Unsecure events. Scott to check 20-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04-Apr-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 18/04/24 retested - Door operated as expected, no UDO when card reader is swiped. When card is swiped and the door is held open the UDO becomes active after 30 seconds and the door status remains open | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 606 Door 29 23/1/24 Unauthorised event yet to be configured in Forcefield. DOTL added as an Input event 16/2/24 Forcefield only sending an Entry event and not the Secure/Unsecure events 20/2/24 All OK (DOTL Input 013 not 13) | Complete |  | Ok*
14 | AEN_DOR_B2_403-1_2 | West Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 20/02/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. Physically the door can't be opened when unlocked using swipe card. 2. Lock / unlock status is received just taping on swipe card. 3. Open and close status is not working. 4. DOTL not working 5.Door opened using push bar without swipping the card , but unauthorised event doesn't come through. Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure 16-Feb-2024: UDO - Card reader events not coming through from forcefield. Scott to check 20-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04-Apr-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. Non CMS issue : 1. Open / Closed read switch showing open when door closed. Leaning on the door while closed gives the closed event. CYP defect ETA ?. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 606 Door 31 23/01/2024 Open / Closed read switch showing open when door closed. Leaning on the door while closed gives the closed event. CYP defect. Unautorised event not yet configured 16/2/24 Card reader events not coming through 20/2/24 All OK. Limit switch still sensitive though. Door needs to be leaned on for close to come through | Complete |  | Ok*
18 | AEN_DOR_B2_403-1_1 | West Emergency Stairs - Platform | MON | N/A | N/A |  |  |  | 23/01/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. Physically the door can't be opened when unlocked using swipe card. 2. Lock / unlock status is received just taping on swipe card. 3. Open and close status is not working. 4. DOTL not working 5.Door opened using push bar without swipping the card , but unauthorised event doesn't come through. Unauthorised event is not confgured in forcefield. With RNA Design & Scott to reconfigure 16-Feb-2024: UDO - Forcefield only sends entry event and not the Secure/Unsecure events. Scott to check 20-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04-Apr-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 18/04/24 Door retested - Alarm when no card reader, No alarm when card reader, after 30 seconds alarm when cardreader door status remains open. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 606 Door 30 23/1/24 Unauthorised event yet to be configured in Forcefield. DOTL added as an Input event 16/2/24 Forcefield only sending an Entry event and not the Secure/Unsecure events 20/2/24 All OK (DOTL Input 011 not 11) | Complete |  | Ok*
29 | AEN_DOR_B1_ESC_STAIRS_04_2 | East Emergency Stairs - Concourse | CON | [5 empty] | 1/02/2024 29/02/2024 | Passed |  |  | [SS] 17/01 - On Challenger |  | 1/2/24 No events coming through at all initially - Updated addresses as per Forcefield | Complete |  | Ok
27 | AEN_DOR_B1_ESC_STAIRS_03_2 | West Emergency Stairs - Concourse | CON | [5 empty] | 2024-03-05 | Passed |  | RSW wired incorrectly (status is inverted - door reports open when closed). CYP defect? 20-Feb-2024: Lock wiring issue? Lock ELL1090 marked as Failed in OCS completions list 29-Feb-2024: Field issues cleared by Chris. CMS receives opened and unlocked when the door is closed and locked. When the door is open, CMS receives locked and unlocked status correctly. Scott will work with Chris to fix the configuration issues. | [SS] 17/01 - On Challenger 09/02/24 - see delivery CKL result in "Delivery Circuit tests" sheet |  | Panel 602 Door 36 1/2/24 RSW wired incorrectly (inverted) - Input 151 on Panel 602 - CYP defect Door events are thus reporting open with door is closed 20/2/24 Mortice lock wired incorrectly not the RSW. Door events are reversed - Christian to look into wiring 5/3/24 Retested OK after Christian fixed issues | Complete |  | Ok
26 | AEN_DOR_B1_ESC_STAIRS_03_1 | West Emergency Stairs - Concourse | CON | [5 empty] | 1/02/2024 10/4/2024 | Failed |  | 10 Apr 2024 : Lock / unlock status is not working, was ok in the past. Defective Lock is the issue. DOTL alarm on CMS appears all the time. 18/04/24 Defective lock to be fixed Friday 19/04/24 | [SS] 17/01 - On Challenger |  | 1/2/24 Forcefield config changes were required. Door left in an unlocked state from Forcefield so people can use without swipe card 11/4/24 DOTL alarm cleared manually as it is no longer be triggered by Forcefield | Complete |  | Ok
1 | AEN_DOR_B1_ESC_STAIR_04_1 | East Emergency Stairs - Concourse | CON | [5 empty] | 29/02/2024 26/03/2024 04/04/2024 10/04/2024 | Failed |  | 1. Swipe card reader is not working. LED's of card reader is off . Lock/ unlock status hasn't not been checked using swipe card. CYP defect ETA?. 2. Open and Close status is not working. 15 Feb 2024: CRD 1083 Swipe card reader is on. However, door is not unlocking using swipe card. Using remote unlock, it is possible to unlock and open the door. To be checked if card reader still has any fault and whether it is sending continual events to forcefield as observed on 01 Feb 2024. Lock/Unlock status - Now not working. It was ok before. Open/Close status - Now not working. It was ok before. DOTL - Still not ok. It was working before. 26 Mar 2024: Work was being carried out on this door. Re-test once the work is completed. Non-NAC door. Design limitation for implementing UDO/Forced door open alarm in forcefield acc. to Scott. 04 Apr 2024: Door marked as "Damaged Do Not Open" 10 Apr 2024: Open / Close status is not working. Field wiring issue after replacement of damaged door. | Known defect against CYP in Omtrak |  | 2. Forcefield vs CMS config to be checked. Door not connected to NAC, so Unauthorised event not possible. 1/2/24 DOTL no longer working. Card reader fault - sending continual events to Forcefield 20/2/24 Swipe card not working | Complete |  | Ok
15 | AEN_DOR_B1_151-4_1 | East BOH Corridor Entry - Concourse | MON | N/A | N/A |  |  |  | 20/02/2024 26/03/2024 04/04/2024 10/04/2024 | Passed |  | 1. Physically door is not locked . We can open from either side without unlocking. 2. Lock/unlock status is not working. 3. Open and close status is not working. 4. DOTL not working 5.Door opened using push bar without swipping the card , but unauthorised event doesn't come through. Unauthorised event is not configured in forcefield.With RNA Design & Scott to reconfigure 15-Feb-2024: Swipe card reader having issue according to Scott. 20-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. 04 Apr -2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. | 09/02/24: Delivery team complete - T&C to interface to design for resolution of requirements or technical solution - cannot verify build any further |  | Panel 607 Door 23 23/1/24 Unauthorised event yet to be configured in Forcefield. DOTL added as an Input event 20/2/24 All OK | Complete |  | Ok*
28 | AEN_DOR_B1_151-3_1 | West BOH Corridor Entry - Concourse | MON | N/A | N/A | OK |  | OK | 29/02/2024 26/03/2024 04/04/2024 | Passed | Open/Close - Swipe card open no alarm, after holding open for 30 seconds NO UDO alarm Unauthorised Access - Push bar access caused UDO | 16-Feb-2024: Reed switch on second leaf is not working. CYP defect- REED switch magnet is missing. 16-Feb-2024: *UDO was received in CMS. However, this was an interim solution implemented in CMS and needs to be re-tested once the permanent solution is implemented in forcefield. 26-Mar-2024: Forcefield is sending UDO alarm when the door is opened with Swipe card. Scott needs to sort out the issue. | [SS] 17/01 - On Challenger 09/02/24 - see delivery CKL result in "Delivery Circuit tests" sheet |  | 1/2/24 Second read switch failed completions testing - CYP defect 16/2/24 CMS script tested and Unauthorised alarm (not from Forcefield) worked | Complete |  | Ok*

## Drawing Reference
# | Asset ID | Device Description (CMS Use) | Internal/External | Door Reed Switch(s) | EML/ELL Devices | Security equipment location plan no. | Drawing Notes relative to the door
13 | AEN_DOR_B2_ESC_STAIRS_04_1 | East Emergency Stairs - Platform | Internal | RSW1210 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1330 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
14 | AEN_DOR_B2_403-1_2 | West Emergency Stairs - Platform | Internal | RSW1232 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1327 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
15 | AEN_DOR_B1_151-4_1 | East BOH Corridor Entry - Concourse | Internal | RSW1159, RSW1160 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1324 | 3. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 4. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
16 | AEN_DOR_B2_ESC_STAIRS_04_2 | East Emergency Stairs - Platform | Internal | RSW1211 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1330 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
17 | AEN_DOR_B2_ESC_STAIRS_03_2 | West Emergency Stairs - Platform | Internal | RSW1234, RSW1235 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1327 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
18 | AEN_DOR_B2_403-1_1 | West Emergency Stairs - Platform | Internal | RSW1231 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1327 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
19 | AEN_DOR_B2_ESC_STAIRS_03_1 | West Emergency Stairs - Platform | Internal | RSW1233 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1327 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
20 | AEN_DOR_B2_ESC_STAIRS_04_4 | East Emergency Stairs - Platform | Internal | RSW1212 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1330 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
21 | AEN_DOR_B2_ESC_STAIRS_04_3 | East Emergency Stairs - Platform | Internal | RSW1213, RSW1214 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1330 | 5. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 6. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
28 | AEN_DOR_B1_151-3_1 | West BOH Corridor Entry - Concourse | Internal | RSW1107, RSW1108 | - | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1323 | 7. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS. 8. THIS DOOR SHALL ALWAYS BE ACCESSIBLE FOR EGRESS PURPOSES. PASSENGERS CAN USE THE PANIC BAR FOR EVACUATION. THE CARD READER SHALL BE USED TO DETERMINE IF UNAUTHORISED PERSONS ENTER A BOH AREA. IF A CARD SWIPE IS NOT DETECTED AND THE DOOR IS OPENED VIA THE PANIC BAR, AN ALARM SHALL BE RAISED.
11 | AEN_DOR_L2_ESC_STAIRS_5_2 | East Emergency Stairs - Level 2 | Internal | RSW1001 | ELL1001 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1332 | -
23 | AEN_DOR_GF_405-2_2 | East Emergency Stairs - Ground Floor | Internal | RSW1032 | ELL10011 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -
10 | AEN_DOR_L1_ESC_STAIRS_5_1 | East Emergency Stairs - Level 1 | Internal | RSW1011 | ELL1002 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1331 | -
6 | AEN_DOR_GF_401-1_1 | Fire Control Room Entry - Ground Floor | External | RSW1223 | ELL1003 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1400 | -
12 | AEN_DOR_LG_ESC_STAIR_07_1 | West Emergency Stairs - Lower Ground Floor | Internal | RSW1079 | ELL1023 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1320 | -
26 | AEN_DOR_B1_ESC_STAIRS_03_1 | West Emergency Stairs - Concourse | Internal | RSW1146 | ELL1034 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1322 | 3. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
1 | AEN_DOR_B1_ESC_STAIR_04_1 | East Emergency Stairs - Concourse | Internal | RSW1161 | ELL1035 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1325 | -
8 | AEN_DOR_GF_ESC_STAIR_9_1 | After hours access - Ground Floor | External | RWG1128, RWG1130 | ELL1082 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | 5. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 6. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
7 | AEN_DOR_GF_405-2_1 | Fire Escape Corridor - Ground Floor | External | RWG1126, RWG1127 | ELL1084 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | 5. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 6. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
2 | AEN_DOR_GF_246-1_1 | West Loading Bay Entry - Ground Floor | External | RSW1058, RSW1059 | ELL1086 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1318 | 4. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 7. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
3 | AEN_DOR_GF_246-1_2 | West Loading Bay Entry - Ground Floor | External | RSW1060, RSW1061 | ELL1087 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1318 | 4. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 7. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
27 | AEN_DOR_B1_ESC_STAIRS_03_2 | West Emergency Stairs - Concourse | Internal | RSW1144, RSW1145 | ELL1090 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1322 | 2. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 3. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
29 | AEN_DOR_B1_ESC_STAIRS_04_2 | East Emergency Stairs - Concourse | Internal | RSW1250, RSW1251 | ELL1093 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1326 | 1. THIS LEAF OF THE DOUBLE DOOR WILL BE PROVIDED WITH MECHANICAL LOCKING INTEGRATED WITH THE PANIC BAR AND SHALL NOT BE PROVIDED WITH ELECTRONIC ACCESS CONTROL. 2. A PANIC BAR SHALL BE FITTED ON THIS DOOR FOR EMERGENCY EGRESS.
9 | AEN_DOR_GF_151-12_1 | Access to office - Ground Floor | Internal | RSW1033, RSW1034 | EML1006 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -
24 | AEN_DOR_LG_405-3_2 | Fire escape Corridor - Lower Ground Floor | Internal | RSW1051, RSW1052 | EML1009 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1321 | -
25 | AEN_DOR_LG_405-3_1 | Fire escape Corridor - Lower Ground Floor | Internal | RSW1053, RSW1054 | EML1010 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1321 | -
4 | AEN_DOR_GF_246-2_1 | East Loading Bay Entry - Ground Floor | External | RSW1151, RSW1152 | EML1077 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -
5 | AEN_DOR_GF_246-2_2 | East Loading Bay Entry - Ground Floor | External | RSW1153, RSW1154 | EML1078 | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -
22 | AEN_ROL_GF_102-1_1 | Main Entrance Roller Door - Ground Floor | External | RWG1001, RWG1002 | N/A | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -
30 | AEN_ROL_GF_102-1_2 | Main Entrance Roller Door - Ground Floor | External | RWG1002 | N/A | RSA-CPBB-SDU-S0900-DRG-LOC-AEN-L1319 | -

## Doors Ready
This sheet does a vlookup of the individual door elements to see if the door itself is ready (all elements have passed)
AssetID | DoorReedSwitch(s) |  | DoorReedSwitch(s) |  | EML/ELLDevices |  | Ready for CMS Testing | CMS Testing Status
AEN_DOR_B1_151-3_1 | RSW1107 | PASS | RSW1108 | FAIL | - |  |  | INCOMPLETE
AEN_DOR_B1_151-4_1 | RSW1159 | PASS | RSW1160 | PASS | - |  | READY | INCOMPLETE
AEN_DOR_B1_ESC_STAIR_04_1 | RSW1161 | PASS |  |  | ELL1035 | FAIL |  | INCOMPLETE
AEN_DOR_B1_ESC_STAIRS_03_1 | RSW1146 | PASS |  |  | ELL1034 | Fail |  | INCOMPLETE
AEN_DOR_B1_ESC_STAIRS_03_2 | RSW1144 | PASS | RSW1145 | PASS | ELL1090 | Fail |  | INCOMPLETE
AEN_DOR_B1_ESC_STAIRS_04_2 | RSW1250 | PASS | RSW1251 | PASS | ELL1093 | PASS | READY | INCOMPLETE
AEN_DOR_B2_403-1_1 | RSW1231 | PASS |  |  | - |  | READY | INCOMPLETE
AEN_DOR_B2_403-1_2 | RSW1232 | FAIL |  |  | - |  |  | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_03_1 | RSW1233 | PASS |  |  | - |  | READY | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_03_2 | RSW1234 | PASS | RSW1235 | PASS | - |  | READY | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_04_1 | RSW1210 | PASS |  |  | - |  | READY | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_04_2 | RSW1211 | PASS |  |  | - |  | READY | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_04_3 | RSW1213 | PASS | RSW1214 | PASS | - |  | READY | INCOMPLETE
AEN_DOR_B2_ESC_STAIRS_04_4 | RSW1212 | PASS |  |  | - |  | READY | INCOMPLETE
AEN_DOR_GF_151-12_1 | RSW1033 | PASS | RSW1034 | PASS | EML1006 | PASS | READY | INCOMPLETE
AEN_DOR_GF_246-1_1 | RSW1058 | PASS | RSW1059 | PASS | ELL1086 | FAIL |  | INCOMPLETE
AEN_DOR_GF_246-1_2 | RSW1060 | PASS | RSW1061 | PASS | ELL1087 | PASS | READY | INCOMPLETE
AEN_DOR_GF_246-2_1 | RSW1151 | PASS | RSW1152 | PASS | EML1077 | PASS | READY | INCOMPLETE
AEN_DOR_GF_246-2_2 | RSW1153 | PASS | RSW1154 | PASS | EML1078 | PASS | READY | INCOMPLETE
AEN_DOR_GF_401-1_1 | RSW1223 | PASS |  |  | ELL1003 | PASS | READY | INCOMPLETE
AEN_DOR_GF_405-2_1 | RWG1126 | PASS | RWG1127 | PASS | ELL1084 | PASS | READY | INCOMPLETE
AEN_DOR_GF_405-2_2 | RSW1032 | PASS |  |  | ELL10011 |  | READY | INCOMPLETE
AEN_DOR_GF_ESC_STAIR_9_1 | RWG1128 | PASS | RWG1130 | PASS | ELL1082 | PASS | READY | INCOMPLETE
AEN_DOR_L1_ESC_STAIRS_5_1 | RSW1011 | PASS |  |  | ELL1002 | PASS | READY | INCOMPLETE
AEN_DOR_L2_ESC_STAIRS_5_2 | RSW1001 | PASS |  |  | ELL1001 | PASS | READY | INCOMPLETE
AEN_DOR_LG_405-3_1 | RSW1053 | PASS | RSW1054 | PASS | EML1010 | PASS | READY | INCOMPLETE
AEN_DOR_LG_405-3_2 | RSW1051 | PASS | RSW1052 | PASS | EML1009 | PASS | READY | INCOMPLETE
AEN_DOR_LG_ESC_STAIR_07_1 | RSW1079 | PASS |  |  | ELL1023 | fail |  | INCOMPLETE
AEN_ROL_GF_102-1_1 | RWG1001 | PASS |  |  | N/A |  | READY | INCOMPLETE
AEN_ROL_GF_102-1_2 | RWG1002 | PASS |  |  | N/A |  | READY | INCOMPLETE

## Copy of Completions Device List
DEVICE | LEVEL | ROOM ID | RACK/CABINET | LOCATION | TEST SCRIPT | COMPLETE/ STATUS | COMMENTS MW | COMMENTS BG
4LC1001 | B2 | 104-01 | LCC01 | B2 Platform - Lift | PANELS & CONTROLLERS | INCOMPLETE | NO ACCESS need Key to open panels |  | PASS
4LC1002 | B2 | 104-01 | LCC02 | B2 Platform - Lift | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K |  | FAIL
4LC1003 | B1 | 103-02 | LCC03 | B1 Concourse - East Lift | PANELS & CONTROLLERS | FAIL | NO COMMUNICATION BACK TO FF, POSSIBLE LAN CARD FAILURE |  | INCOMPLETE
4LC1004 | B1 | 103-02 | LCC04 | B1 Concourse - East - Lift | PANELS & CONTROLLERS | FAIL | NO COMMUNICATION BACK TO FF, POSSIBLE LAN CARD FAILURE |  | NOT STARTED
4LC1005 | GF | S-03 | LCC05 | LIFT 5 | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K | ELM 100% complete | N/A
4LC1006 | LG | 405-03 | LCC06 | Lift 6 | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
BGR1002 | L2 | 803-03 | DGP1001 |  | DETECTION & EGRESS | PASS
BGR1003 | L2 | 802-02 | DGP1001 |  | DETECTION & EGRESS | N/A |  | R
BGR1005 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1014 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1015 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1016 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1018 | GF | 151-12 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1021 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | DETECTION & EGRESS | PASS
BGR1022 | LG | 812-02 | DGP1007 | Mech PLANT - LG - WEST | DETECTION & EGRESS | PASS
BGR1023 | LG | 812-02 | DGP1007 |  | DETECTION & EGRESS | PASS
BGR1025 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | DETECTION & EGRESS | PASS
BGR1026 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | DETECTION & EGRESS | PASS
BGR1027 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | DETECTION & EGRESS | PASS
BGR1030 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
BGR1032 | B1 | 803-01 | DGP1013 |  | DETECTION & EGRESS | FAIL | NOT REGISTERING IN FORCEFIELD
BGR1033 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | DETECTION & EGRESS | N/A |  | R
BGR1034 | B1 | 830-01 | DGP1020 |  | DETECTION & EGRESS | PASS
BGR1039 | B1 | 234-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
BGR1040 | B1 | 230-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
BGR1041 | B1 | 231-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
BGR1045 | B1 | 151-09 | DGP1015 |  | DETECTION & EGRESS | PASS
BGR1046 | B1 | 705-01 | DGP1015 |  | DETECTION & EGRESS | N/A |  | R
BGR1047 | B1 | 501-01 | DGP1015 | SER | DETECTION & EGRESS | N/A |  | R
BGR1051 | B1 | 611-02 | DGP1007 |  | DETECTION & EGRESS | N/A |  | R
BGR1052 | B1 | 650-01 | DGP1008 |  | DETECTION & EGRESS | PASS
BGR1053 | B1 | 650-02 | DGP1008 |  | DETECTION & EGRESS | PASS
BGR1054 | B1 | 611-01 | DGP1007 |  | DETECTION & EGRESS | N/A |  | R
BGR1055 | B1 | 640-04 | DGP1008 |  | DETECTION & EGRESS | PASS
BGR1056 | B1 | 640-03 | DGP1009 |  | DETECTION & EGRESS | PASS
BGR1058 | B1 | 652-02 | DGP1016 |  | DETECTION & EGRESS | PASS
BGR1059 | B1 | 830-03 | DGP1010 |  | DETECTION & EGRESS | PASS
BGR1060 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | DETECTION & EGRESS | N/A |  | R
BGR1061 | B1 | 803-02 | DGP1009 |  | DETECTION & EGRESS | FAIL | ISSUES WITH WIRING FOR ALL ON THIS DOOR/ROOM 803-2
BGR1062 | B1 | 831-02 | DGP1010 |  | DETECTION & EGRESS | FAIL | NOT REGISTEREING IN FORCEFIELD
BGR1065 | B2 | 651-03 | DGP1018 |  | DETECTION & EGRESS | PASS
BGR1066 | B2 | 651-01 | DGP1018 |  | DETECTION & EGRESS | PASS
BGR1067 | B2 | 151-05 | DGP1019 |  | DETECTION & EGRESS | PASS
BGR1080 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
BGR1081 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
BGR1082 | B2 | 651-04 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
BGR1083 | B2 | 651-02 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
BGR1084 | GF | 405-02 | DGP1002 |  | DETECTION & EGRESS | N/A | PUSHBAR | R
BGR1085 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1086 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% pass on ELM
BGR1087 | GF | S-09 | DGP1002 |  | DETECTION & EGRESS | N/A |  | R
BGR1088 | LG | 239-01 | DGP1016 |  | DETECTION & EGRESS | PASS
BGR1089 | GF | 401-01 | DGP1003 |  | DETECTION & EGRESS | N/A |  | R
CRD1001 | L2 | S-05 | NAC1001 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1002 | L2 | 811-04 | NAC1001 |  | ACCESS & ARMING | PASS
CRD1003 | L2 | 803-03 | NAC1001 |  | ACCESS & ARMING | PASS
CRD1004 | L2 | 802-02 | NAC1001 |  | ACCESS & ARMING | PASS
CRD1005 | L1 | S-05 | NAC1001 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1008 | L1 | 710-03 | NAC1001 |  | ACCESS & ARMING | PASS | SKIP FORCED DOOR
CRD1012 | L1 | 211-01 | NAC1001 | ICR L1 EAST | ACCESS & ARMING | PASS | SKIP FORCED DOOR | SKIP FORCED DOOR
CRD1014 | L1 | 201-01 | NAC1002 | SCR L1 EAST | ACCESS & ARMING | PASS
CRD1015 | L1 | 204-01 | NAC1002 | SMO L1 EAST | ACCESS & ARMING | PASS | SKIP, FORCED DOOR
CRD1016 | GF | S-05 | NAC1002 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs | 100% complete on ELM
CRD1017 | GF | 151-12 | NAC1002 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1018 | GF | 306-01 | NAC1003 |  | ACCESS & ARMING | PASS | FORCED DOOR OK | 100% complete on ELM
CRD1019 | GF | 202-01 | NAC1003 |  | ACCESS & ARMING | PASS | FORCED DOOR OK | 100% complete on ELM
CRD1022 | LG | 234-02 | NAC1007 |  | ACCESS & ARMING | PASS | FORCED DOOR OK
CRD1023 | GF | 405-02 | NAC1002 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1025 | LG | 812-02 | NAC1007 |  | ACCESS & ARMING | PASS | FORCED DOOR OK
CRD1026 | LG | 812-02 | NAC1007 |  | ACCESS & ARMING | PASS
CRD1027 | GF | 650-03 | NAC1004 | LV Switch Room A2 - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1028 | GF | 650-03 | NAC1004 | LV Switch Room A2 - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1029 | GF | 610-01 | NAC1004 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1030 | GF | 610-01 | NAC1004 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1031 | GF | 610-02 | NAC1006 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1032 | GF | 246-01 | NAC1005 | GF - Loading bay - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1033 | GF | 246-01 | NAC1005 | GF - Loading bay - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1034 | GF | S-03 | NAC1005 | ESC STAIRS - GF - WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs | 100% complete on ELM
CRD1035 | GF | S-03 | NAC1005 | ESC STAIRS - GF - WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1036 | GF | S-03 | NAC1005 | ESC STAIRS - GF - WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1037 | GF | 706-01 | NAC1006 | Telephone Equipment Room - GF West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1038 | GF | 709-03 | NAC1005 | COMMS CPB GF WEST | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1039 | GF | 409-05 | NAC1005 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1040 | GF | 650-04 | NAC1004 | LV Switch Room B2 - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1041 | GF | 650-04 | NAC1004 | LV Switch Room B2 - West | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1042 | GF | S-09 | NAC1002 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs | 100% complete on ELM
CRD1043 | LG | 802-01 | NAC1006 | Fire Suppresion Room LG - West | ACCESS & ARMING | PASS
CRD1044 | LG | S-07 | NAC1006 | ESC STAIRS - LG - WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1045 | B1 | 640-01 | NAC1019 | UBS Battery Room A - West | ACCESS & ARMING | PASS
CRD1046 | B1 | 640-01 | NAC1019 | UBS Battery Room A - West | ACCESS & ARMING | PASS
CRD1047 | B1 | 640-02 | NAC1011 | UBS Battery Room B - West | ACCESS & ARMING | PASS
CRD1048 | B1 | 640-02 | NAC1011 | UBS Battery Room B - West | ACCESS & ARMING | PASS
CRD1049 | B1 | 409-01 | NAC1011 | Fire Suppresion Room B1 - West | ACCESS & ARMING | PASS
CRD1050 | B1 | 652-01 | NAC1011 | TVS MCC ROOM A - West | ACCESS & ARMING | PASS
CRD1051 | B1 | 652-01 | NAC1011 | TVS MCC ROOM A - West | ACCESS & ARMING | PASS
CRD1052 | B1 | 602-01 | NAC1012 |  | ACCESS & ARMING | PASS
CRD1053 | B1 | 602-01 | NAC1012 |  | ACCESS & ARMING | PASS
CRD1054 | B1 | 602-02 | NAC1012 |  | ACCESS & ARMING | PASS
CRD1055 | B1 | 602-02 | NAC1012 |  | ACCESS & ARMING | PASS
CRD1056 | B1 | 602-03 | NAC1011 |  | ACCESS & ARMING | PASS
CRD1057 | B1 | 602-03 | NAC1011 |  | ACCESS & ARMING | PASS
CRD1058 | B1 | 811-01 | NAC1012 |  | ACCESS & ARMING | PASS | no egress, no forced door N/A
CRD1059 | B1 | 234-01 | NAC1014 |  | ACCESS & ARMING | PASS
CRD1060 | B1 | 230-01 | NAC1014 |  | ACCESS & ARMING | PASS
CRD1061 | B1 | 231-01 | NAC1014 |  | ACCESS & ARMING | PASS
CRD1062 | B1 | 151-10 | NAC1014 |  | ACCESS & ARMING | PASS
CRD1063 | B1 | 151-09 | NAC1015 |  | ACCESS & ARMING | PASS
CRD1065 | B1 | 245-01 | NAC1015 |  | ACCESS & ARMING | FAIL | dotl fail, egress n/a, forced door n/a
CRD1066 | B1 | 705-01 | NAC1015 |  | ACCESS & ARMING | PASS
CRD1067 | B1 | 811-02 | NAC1015 |  | ACCESS & ARMING | PASS
CRD1068 | B1 | 501-01 | NAC1015 | SER | ACCESS & ARMING | PASS
CRD1069 | GF | 401-01 | NAC1003 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1070 | B1 | 704-01 | NAC1015 |  | ACCESS & ARMING | PASS
CRD1072 | GF | 401-01 | NAC1003 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1075 | B1 | 831-01 | NAC1013 |  | ACCESS & ARMING | PASS
CRD1076 | B1 | 831-01 | NAC1013 |  | ACCESS & ARMING | PASS
CRD1077 | B1 | S-03 | NAC1013 | ESC STAIRS - B1 WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1078 | B1 | 803-01 | NAC1013 |  | ACCESS & ARMING | PASS
CRD1079 | B1 | S-03 | NAC1013 | ESC STAIRS - B1 WEST | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1080 | B1 | 830-02 | NAC1020 | TVCS FAN ROOM - B1 - West | ACCESS & ARMING | N/A |  | R
CRD1081 | B1 | 830-01 | NAC1020 |  | ACCESS & ARMING | PASS
CRD1082 | B1 | 151-04 | NAC1007 | EAST - BOH CORRIDOR 04 | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up
CRD1083 | B1 | S-04 | NAC1007 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1085 | B1 | 652-02 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1086 | B1 | 652-02 | NAC1016 |  | ACCESS & ARMING | PASS | DOLT WORKS ON FF, BUT NO SOUND ON-SITE
CRD1087 | B1 | 611-02 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1088 | B1 | 650-01 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1089 | B1 | 650-01 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1090 | B1 | 650-02 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1091 | B1 | 650-02 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1092 | B1 | 611-01 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1093 | B1 | 611-01 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1094 | B1 | 640-04 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1095 | B1 | 640-04 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1096 | B1 | 640-03 | NAC1008 |  | ACCESS & ARMING | PASS
CRD1097 | B1 | 640-03 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1098 | B1 | 409-04 | NAC1010 |  | ACCESS & ARMING | FAIL | DOTL not registering
CRD1099 | B1 | 830-03 | NAC1010 |  | ACCESS & ARMING | PASS
CRD1100 | B1 | 830-04 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ACCESS & ARMING | N/A |  | R
CRD1101 | B1 | 803-02 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1102 | B1 | 831-02 | NAC1010 |  | ACCESS & ARMING | PASS
CRD1103 | B1 | 831-02 | NAC1010 |  | ACCESS & ARMING | pass | FAIL DOOR FORCED
CRD1105 | B2 | 710-02 | NAC1021 |  | ACCESS & ARMING | PASS
CRD1106 | B2 | S-04 | NAC1016 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs | Not configured locally
CRD1107 | B2 | S-04 | NAC1016 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1108 | B2 | S-04 | NAC1021 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1109 | B2 | S-04 | NAC1021 |  | ACCESS & ARMING | FAIL | Card reader for alarm control only. Alarms not set up, same for all eress stairs
CRD1110 | B2 | 151-15 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1111 | B2 | 151-16 | NAC1016 |  | ACCESS & ARMING | PASS
CRD1112 | B2 | 151-16 | NAC1016 |  | ACCESS & ARMING | PASS
CRD1113 | B2 | 151-15 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1114 | B2 | 601-02 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1115 | B2 | 601-02 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1116 | B2 | 151-6 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1117 | B2 | 651-02 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1118 | B2 | 651-04 | NAC1017 |  | ACCESS & ARMING | PASS
CRD1119 | B2 | 710-01 | NAC1021 |  | ACCESS & ARMING | PASS
CRD1120 | B2 | 403-01 | NAC1019 |  | ACCESS & ARMING | FAIL | NOT PROGRAMMED IN FF
CRD1121 | B2 | 403-01 | NAC1019 |  | ACCESS & ARMING | FAIL | not pROGRAMMED IN FF
CRD1122 | B2 | 403-01 | NAC1019 |  | ACCESS & ARMING | FAIL | card reader not setup correctly per egress
CRD1123 | B2 | 403-01 | NAC1019 |  | ACCESS & ARMING | FAIL | NOT INSTALLED
CRD1124 | B2 | 151-07 | NAC1018 |  | ACCESS & ARMING | PASS
CRD1125 | B2 | 151-05 | NAC1019 |  | ACCESS & ARMING | PASS
CRD1127 | B2 | 151-07 | NAC1018 |  | ACCESS & ARMING | FAIL | DOTL FAIL ON FF
CRD1130 | B2 | 651-01 | NAC1018 |  | ACCESS & ARMING | PASS
CRD1131 | B2 | 651-03 | NAC1018 |  | ACCESS & ARMING | PASS
CRD1132 | B2 | 601-01 | NAC1018 |  | ACCESS & ARMING | PASS | CARD READER NOT SECURED TO WALL
CRD1133 | B2 | 409-03 | NAC1018 |  | ACCESS & ARMING | PASS
CRD1134 | B2 | 601-01 | NAC1018 |  | ACCESS & ARMING | PASS
CRD1135 | GF | 246-02 | NAC1003 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1136 | GF | 246-02 | NAC1003 |  | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1137 | GF | 811-03 | NAC1006 | HVAC PLANT - GF - WEST | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1141 | LFT | LIFT-0001 | 4LC1001 | LIFT 1 | ACCESS & ARMING | PASS | Card readers accept swipe, but have no programmed functions as per design
CRD1142 | B2 | LIFT-0002 | 4LC1002 | LIFT 2 | ACCESS & ARMING | PASS | Card readers accept swipe, but have no programmed functions as per design
CRD1143 | GF | LIFT-0003 | 4LC1003 | LIFT 3 | ACCESS & ARMING | PASS | Card readers accept swipe, but have no programmed functions as per design | 100% complete on ELM
CRD1144 | GF | 103-01 | 4LC1003 | Lift 1/2 | ACCESS & ARMING | PASS | Card readers accept swipe, but have no programmed functions as per design | 100% complete on ELM
CRD1145 | GF | LIFT-0004 | 4LC1004 | LIFT 4 | ACCESS & ARMING | PASS | Card readers accept swipe, but have no programmed functions as per design | 100% complete on ELM
CRD1146 | GF | LIFT-0005 | 4LC1005 | LIFT 5 | ACCESS & ARMING | PASS | ACCESS GRANTED | 100% complete on ELM
CRD1147 | GF | 103-01 | 4LC1005 | Lift 5 | ACCESS & ARMING | PASS | ACCESS GRANTED | 100% complete on ELM
CRD1148 | LG | LIFT-0006 | 4LC1006 | LIFT 6 | ACCESS & ARMING | FAIL | INTERNAL CARD FAULTY
CRD1149 | GF | LIFT-0006 | 4LC1006 | LIFT 6-G1 | ACCESS & ARMING | PASS |  | 100% complete on ELM
CRD1163 | GF | 102-01 | NAC1002 |  | ACCESS & ARMING | FAIL | NO POWER CONNECTED
CRD1164 | B1 | 831-01 | NAC1013 | OTE FAN ROM - B1 - WEST | ACCESS & ARMING | PASS
CRD1165 | B1 | 831-02 | NAC1009 | OTE FAN ROM - B1 - EAST | ACCESS & ARMING | FAIL | DOTL NOT CLEARING ON FORCEFIELD
CRD1166 | B1 | 831-02 | NAC1009 |  | ACCESS & ARMING | PASS
CRD1167 | B1 | 151-04 | NAC1007 |  | ACCESS & ARMING | PASS
CRD1168 | B1 | 830-01 | NAC1020 |  | ACCESS & ARMING | PASS
CRD1169 | B1 | 830-04 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ACCESS & ARMING | N/A |  | R
CRD1170 | B1 | 830-03 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ACCESS & ARMING | N/A |  | R
CRD1171 | B1 | 830-01 | NAC1020 |  | ACCESS & ARMING | N/A |  | R
CRD1172 | B1 | 830-02 | NAC1020 | TVCS FAN ROOM - B1 - West | ACCESS & ARMING | N/A |  | R
CRD1173 | B1 | 151-10 |  | B1 - BOH CORRIDOR to FOH WEST | ACCESS & ARMING | FAIL | CRD not installed (SEE -> RNA-RFI-008336)
CRD1174 | B1 | 151-04 |  | B1 - BOH CORRIDOR to FOH EAST | ACCESS & ARMING | FAIL | CRD not installed (SEE -> RNA-RFI-008336)
CRD1196 | LG | 239-01 | NAC1016 |  | ACCESS & ARMING | PASS
CRD1197 | L1 | 211-01 | NAC1001 | ICR L1 EAST | ACCESS & ARMING | PASS
DGP1001 | L1 | 710-03 | DGP1001 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
DGP1002 | L1 | 710-03 | DGP1002 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
DGP1003 | L1 | 710-03 | DGP1003 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
DGP1004 | GF | 709-03 | DGP1004 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS | TAMPER SWITCH K, POWER K | 100% complete on ELM
DGP1005 | GF | 709-03 | DGP1005 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS |  | 100% complete on ELM
DGP1006 | GF | 709-03 | DGP1006 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS |  | 100% complete on ELM
DGP1007 | B1 | 709-02 | DGP1007 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT, ERROR LOG FOR BATTERIES
DGP1008 | B1 | 709-02 | DGP1008 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT, ERROR LOG FOR BATTERIES
DGP1009 | B1 | 709-02 | DGP1009 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT, ERROR LOG FOR BATTERIES
DGP1010 | B1 | 709-02 | DGP1010 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT, ERROR LOG FOR BATTERIES
DGP1011 | B1 | 704-01 | DGP1011 |  | PANELS & CONTROLLERS | PASS
DGP1012 | B1 | 704-01 | DGP1012 |  | PANELS & CONTROLLERS | PASS
DGP1013 | B1 | 704-01 | DGP1013 |  | PANELS & CONTROLLERS | PASS
DGP1014 | B1 | 704-01 | DGP1014 |  | PANELS & CONTROLLERS | PASS
DGP1015 | B1 | 704-01 | DGP1015 |  | PANELS & CONTROLLERS | PASS
DGP1016 | B2 | 651-02 | DGP1016 |  | PANELS & CONTROLLERS | PASS
DGP1017 | B2 | 651-02 | DGP1017 |  | PANELS & CONTROLLERS | PASS
DGP1018 | B2 | 651-03 | DGP1018 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
DGP1019 | B2 | 651-03 | DGP1019 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
DGP1020 | B2 | 651-03 | DGP1020 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
DGP1021 | B2 | 710-02 | DGP1021 |  | PANELS & CONTROLLERS | PASS | TAMPER K, POWER MAINS FAILURE K
DUR1001 | GF | 202-01 | DGP1003 |  | DETECTION & EGRESS | PASS
DUR1002 | GF | 202-01 | DGP1003 |  | DETECTION & EGRESS | PASS
ELL1001 | L2 | S-05 | NAC1001 |  | ELECTRONIC LOCK | PASS
ELL1002 | L1 | S-05 | NAC1001 |  | ELECTRONIC LOCK | PASS
ELL1003 | GF | 401-01 | NAC1003 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1004 | B1 | 830-01 | NAC1020 |  | ELECTRONIC LOCK | N/A |  | R
ELL1005 | L1 | 710-03 | NAC1001 |  | ELECTRONIC LOCK | PASS
ELL1006 | B1 | 830-02 | NAC1020 | TVCS FAN ROOM - B1 - West | ELECTRONIC LOCK | N/A |  | R
ELL1007 | L1 | 211-01 | NAC1001 | ICR L1 EAST | ELECTRONIC LOCK | PASS
ELL1008 | B1 | 652-02 | NAC1009 |  | ELECTRONIC LOCK | PASS
ELL1009 | L1 | 201-01 | NAC1002 | SCR L1 EAST | ELECTRONIC LOCK | PASS | FORCED DOOR OK
ELL1010 | L1 | 204-01 | NAC1002 | SMO L1 EAST | ELECTRONIC LOCK | PASS
ELL1011 | GF | S-05 | NAC1002 |  | ELECTRONIC LOCK | PASS | RTE ALARM NOT REGISTERING BY DESIGN | 100% complete on ELM
ELL1012 | GF | 306-01 | NAC1003 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1013 | GF | 202-01 | NAC1003 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1014 | B1 | 830-04 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ELECTRONIC LOCK | N/A |  | R
ELL1015 | B1 | 830-03 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ELECTRONIC LOCK | N/A |  | R
ELL1016 | LG | 234-02 | NAC1007 |  | ELECTRONIC LOCK | PASS
ELL1017 | GF | 650-03 | NAC1004 | LV Switch Room A2 - West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1018 | GF | 610-01 | NAC1004 | HV Substation 1 | ELECTRONIC LOCK | FAIL | push bar works mechanically but doesn’t show on FF, not activating/deactivating electronic lock, error log to be raised
ELL1019 | GF | S-03 | NAC1005 | ESC STAIRS - GF - WEST | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1020 | GF | 709-03 | NAC1005 | COMMS CPB GF WEST | ELECTRONIC LOCK | PASS | ACTUAL DOOR LOCK TONGUE IS MISALIGNED , NEED TO SLAM DOOR TO CLOSE | 100% complete on ELM
ELL1021 | GF | 409-05 | NAC1005 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1022 | GF | 650-04 | NAC1004 | LV Switch Room B2 - West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1023 | LG | S-07 | NAC1006 | ESC STAIRS - LG - WEST | ELECTRONIC LOCK | fail | not unlocking when accessed
ELL1024 | B1 | 640-01 | NAC1019 | UBS Battery Room A - West | ELECTRONIC LOCK | PASS
ELL1025 | B1 | 640-02 | NAC1011 | UBS Battery Room B - West | ELECTRONIC LOCK | PASS
ELL1026 | B1 | 409-01 | NAC1011 | Fire Suppresion Room B1 - West | ELECTRONIC LOCK | PASS
ELL1027 | B1 | 652-01 | NAC1011 | TVS MCC ROOM A - West | ELECTRONIC LOCK | PASS
ELL1028 | B1 | 811-01 | NAC1012 |  | ELECTRONIC LOCK | PASS
ELL1029 | L2 | 802-02 | NAC1001 |  | ELECTRONIC LOCK | FAIL | STATUS NOT WORKING. RFI-007549 shows this has been changed from EML to ELL so therefore ELL1029 should be correct
ELL1030 | B1 | 245-01 | NAC1015 |  | ELECTRONIC LOCK | PASS
ELL1031 | B1 | 234-01 | NAC1014 |  | ELECTRONIC LOCK | PASS
ELL1032 | B1 | 230-01 | NAC1014 |  | ELECTRONIC LOCK | PASS
ELL1033 | B1 | 831-01 | NAC1013 |  | ELECTRONIC LOCK | PASS | LOCK STICKING
ELL1034 | B1 | S-03 | NAC1013 | ESC STAIRS - B1 WEST | ELECTRONIC LOCK | Fail | Door Lock not mechanicaly Secure on the inside of the stairs.
ELL1035 | B1 | S-04 | NAC1007 |  | ELECTRONIC LOCK | FAIL | electronic lock not functional
ELL1036 | B1 | 650-01 | NAC1008 |  | ELECTRONIC LOCK | PASS
ELL1037 | B1 | 650-02 | NAC1008 |  | ELECTRONIC LOCK | PASS
ELL1038 | B1 | 611-01 | NAC1009 |  | ELECTRONIC LOCK | PASS
ELL1039 | B1 | 640-04 | NAC1008 |  | ELECTRONIC LOCK | PASS
ELL1040 | B1 | 640-03 | NAC1009 |  | ELECTRONIC LOCK | PASS
ELL1041 | B1 | 409-04 | NAC1010 |  | ELECTRONIC LOCK | PASS
ELL1042 | B1 | 831-02 | NAC1010 |  | ELECTRONIC LOCK | FAIL | FORCED DOOR NOT WORKING IN FORCEFIELD
ELL1043 | B1 | 231-01 | NAC1014 |  | ELECTRONIC LOCK | PASS
ELL1044 | B1 | 705-01 | NAC1015 |  | ELECTRONIC LOCK | FAIL | FAIL DOOR FORCED
ELL1046 | B2 | 151-15 | NAC1017 |  | ELECTRONIC LOCK | FAIL | EGRESS FAILS ON FF
ELL1047 | B2 | 151-15 | NAC1017 |  | ELECTRONIC LOCK | FAIL | EGRESS FAILS ON FF
ELL1048 | B2 | 601-02 | NAC1017 |  | ELECTRONIC LOCK | PASS
ELL1049 | B2 | 409-02 | NAC1017 |  | ELECTRONIC LOCK | PASS | RTE NOT APPLICABLE. NO FORCED DOOR
ELL1051 | B1 | 611-01 | NAC1009 |  | ELECTRONIC LOCK | FAIL | push bar works mechanically but doesn’t show on FF, not activating/deactivating electronic lock, error log to be raised
ELL1052 | B1 | 611-02 | NAC1008 |  | ELECTRONIC LOCK | FAIL | push bar works mechanically but doesn’t show on FF, not activating/deactivating electronic lock, error log to be raised
ELL1053 | B2 | 710-01 | NAC1021 |  | ELECTRONIC LOCK | PASS | . Forced door not showing on FF
ELL1054 | B2 | 151-07 | NAC1018 |  | ELECTRONIC LOCK | PASS
ELL1055 | B2 | 151-07 | NAC1018 |  | ELECTRONIC LOCK | PASS
ELL1056 | L2 | 811-04 | NAC1001 |  | ELECTRONIC LOCK | PASS
ELL1057 | B1 | 811-02 | NAC1015 |  | ELECTRONIC LOCK | PASS
ELL1058 | B2 | 409-03 | NAC1018 |  | ELECTRONIC LOCK | PASS
ELL1059 | B2 | 710-02 | NAC1021 |  | ELECTRONIC LOCK | PASS
ELL1060 | GF | 610-01 | NAC1004 |  | ELECTRONIC LOCK | FAIL | push bar works mechanically but doesn’t show on FF, not activating/deactivating electronic lock, error log to be raised | fail here pass on other sheet
ELL1061 | GF | 610-02 | NAC1006 |  | ELECTRONIC LOCK | FAIL | push bar works mechanically but doesn’t show on FF, not activating/deactivating electronic lock, error log to be raised | fail here pass on other sheet
ELL1062 | B1 | 831-01 | NAC1013 |  | ELECTRONIC LOCK | PASS
ELL1063 | B1 | 602-01 | NAC1012 |  | ELECTRONIC LOCK | PASS | PUSH BAR GETS STUCK,UNABLE TO TEST FORCED DOOR
ELL1064 | B1 | 602-01 | NAC1012 |  | ELECTRONIC LOCK | PASS | UNABLE TO TEST FORCED DOOR
ELL1065 | B1 | 602-02 | NAC1012 |  | ELECTRONIC LOCK | PASS | FORCED DOOR CANT BE TESTED
ELL1066 | B1 | 602-02 | NAC1012 |  | ELECTRONIC LOCK | PASS
ELL1067 | B1 | 602-03 | NAC1011 |  | ELECTRONIC LOCK | PASS | PUSH BAR GETS STUCK
ELL1068 | B1 | 602-03 | NAC1011 |  | ELECTRONIC LOCK | PASS | STICKY LOCK
ELL1069 | B2 | 651-04 | NAC1017 |  | ELECTRONIC LOCK | PASS
ELL1070 | B2 | 651-02 | NAC1017 |  | ELECTRONIC LOCK | PASS
ELL1071 | B1 | 831-02 | NAC1009 |  | ELECTRONIC LOCK | PASS
ELL1072 | B1 | 831-02 | NAC1009 |  | ELECTRONIC LOCK | PASS
ELL1073 | B2 | 601-01 | NAC1018 |  | ELECTRONIC LOCK | PASS
ELL1074 | B2 | 601-01 | NAC1018 |  | ELECTRONIC LOCK | PASS
ELL1075 | B2 | 601-02 | NAC1017 |  | ELECTRONIC LOCK | PASS
ELL1076 | B1 | 830-01 | NAC1020 |  | ELECTRONIC LOCK | PASS
ELL1077 | B1 | 501-01 |  | SER |  | PASS
ELL1080 | GF | 401-01 | NAC1003 |  | ELECTRONIC LOCK | PASS
ELL1081 | L1 | 211-01 | NAC1001 | ICR L1 EAST | ELECTRONIC LOCK | PASS
ELL1082 | GF | S-09 | NAC1002 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1084 | GF | 405-02 | NAC1002 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1086 | GF | 246-01 | NAC1005 | GF - Loading bay - West | ELECTRONIC LOCK | FAIL | Door Lock not mechanicaly Secure | STEPS PASS, fail here pass on other sheet
ELL1087 | GF | 246-01 | NAC1005 | GF - Loading bay - West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
ELL1090 | B1 | S-03 | NAC1013 | ESC STAIRS - B1 WEST | ELECTRONIC LOCK | Fail | Door Lock not mechanicaly Secure on the inside of the stairs.
ELL1093 | B1 | 151-04 | NAC1007 | EAST - BOH CORRIDOR 04 | ELECTRONIC LOCK | PASS
ELL1096 | B1 | 704-01 | NAC1015 |  | ELECTRONIC LOCK | PASS
EML1001 | L2 | 803-03 | NAC1001 |  | ELECTRONIC LOCK | PASS
EML1002 | GF | 811-03 | NAC1006 | HVAC PLANT - GF - WEST | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1006 | GF | 151-12 | NAC1002 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1009 | LG | 812-02 | NAC1007 |  | ELECTRONIC LOCK | PASS | NEED TO TEST FORCED LOCK
EML1010 | LG | 812-02 | NAC1007 |  | ELECTRONIC LOCK | PASS | NEED TO TEST FORCED LOCK
EML1011 | GF | 650-03 | NAC1004 | LV Switch Room A2 - West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1018 | GF | 706-01 | NAC1006 | Telephone Equipment Room - GF West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1019 | GF | 650-04 | NAC1004 | LV Switch Room B2 - West | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1021 | LG | 802-01 | NAC1006 | Fire Suppresion Room LG - West | ELECTRONIC LOCK | PASS
EML1022 | B1 | 640-01 | NAC1019 | UBS Battery Room A - West | ELECTRONIC LOCK | PASS
EML1023 | B1 | 640-02 | NAC1011 | UBS Battery Room B - West | ELECTRONIC LOCK | PASS
EML1024 | B1 | 652-01 | NAC1011 | TVS MCC ROOM A - West | ELECTRONIC LOCK | PASS
EML1035 | B1 | 151-09 | NAC1015 |  | ELECTRONIC LOCK | PASS
EML1038 | B1 | 501-01 | NAC1015 | SER | ELECTRONIC LOCK | N/A |  | R
EML1043 | B1 | 831-01 | NAC1013 |  | ELECTRONIC LOCK | PASS
EML1045 | B1 | 803-01 | NAC1013 |  | ELECTRONIC LOCK | FAIL | MAG LOCK NOT WORKING- NO POWER
EML1046 | B1 | 830-02 | NAC1020 | TVCS FAN ROOM - B1 - West | ELECTRONIC LOCK | N/A |  | R
EML1047 | B1 | 830-01 | NAC1020 |  | ELECTRONIC LOCK | PASS
EML1051 | B1 | 652-02 | NAC1016 |  | ELECTRONIC LOCK | PASS
EML1053 | B1 | 650-01 | NAC1008 |  | ELECTRONIC LOCK | PASS
EML1054 | B1 | 650-02 | NAC1008 |  | ELECTRONIC LOCK | PASS
EML1055 | B1 | 611-01 | NAC1009 |  | ELECTRONIC LOCK | N/A |  | R
EML1056 | B1 | 640-04 | NAC1008 |  | ELECTRONIC LOCK | PASS
EML1057 | B1 | 640-03 | NAC1009 |  | ELECTRONIC LOCK | PASS
EML1058 | B1 | 830-03 | NAC1010 |  | ELECTRONIC LOCK | PASS
EML1059 | B1 | 830-04 | NAC1010 | TVCS FAN ROOM - B1 - EAST | ELECTRONIC LOCK | N/A |  | R
EML1060 | B1 | 803-02 | NAC1009 |  | ELECTRONIC LOCK | Pass
EML1061 | B1 | 831-02 | NAC1010 |  | ELECTRONIC LOCK | FAIL | MAG LOCK FAILS- NO POWER
EML1065 | B2 | 151-16 | NAC1016 |  | ELECTRONIC LOCK | FAIL | mag not aligned
EML1066 | B2 | 151-16 | NAC1016 |  | ELECTRONIC LOCK | FAIL | MAG LOCK FAIL, missing mag lock on one side, see photo mag lock on other side not contact correctly
EML1068 | B2 | 651-02 | NAC1017 |  | ELECTRONIC LOCK | N/A |  | R
EML1069 | B2 | 651-04 | NAC1017 |  | ELECTRONIC LOCK | N/A |  | R
EML1072 | B2 | 151-05 | NAC1019 |  | ELECTRONIC LOCK | PASS | only 1 mag on this door
EML1073 | B2 | 651-01 | NAC1018 |  | ELECTRONIC LOCK | PASS
EML1074 | B2 | 651-03 | NAC1018 |  | ELECTRONIC LOCK | PASS
EML1077 | GF | 246-02 | NAC1003 |  | ELECTRONIC LOCK | PASS |  | 100% complete on ELM
EML1078 | GF | 246-02 | NAC1003 |  | ELECTRONIC LOCK | PASS
EML1080 | LG | 239-01 | NAC1016 |  | ELECTRONIC LOCK | PASS | FORCED DOOR TO BE TESTED
EML1082 | GF | S-09 | NAC1002 |  | ELECTRONIC LOCK | N/A |  | R
EML1083 | GF | 401-01 | NAC1003 |  | ELECTRONIC LOCK | N/A |  | R
EML1084 | GF | 405-02 | NAC1002 |  | ELECTRONIC LOCK | N/A |  | R
KOR1001 | L2 | 803-03 | DGP1001 |  | DETECTION & EGRESS | PASS
KOR1002 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | DETECTION & EGRESS | PASS |  | not in the execution list
KOR1003 | L2 | 802-02 | DGP1001 |  | DETECTION & EGRESS | N/A |  | R
KOR1006 | GF | 151-12 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1009 | LG | 812-02 | DGP1007 |  | DETECTION & EGRESS | PASS
KOR1010 | LG | 812-02 | DGP1007 |  | DETECTION & EGRESS | PASS
KOR1011 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1018 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1019 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1021 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | DETECTION & EGRESS | PASS
KOR1022 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | DETECTION & EGRESS | PASS
KOR1023 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | DETECTION & EGRESS | PASS
KOR1024 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | DETECTION & EGRESS | PASS
KOR1031 | B1 | 234-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
KOR1032 | B1 | 230-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
KOR1033 | B1 | 231-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
KOR1035 | B1 | 151-09 | DGP1015 |  | DETECTION & EGRESS | PASS
KOR1036 | B1 | 705-01 | DGP1015 |  | DETECTION & EGRESS | N/A |  | R
KOR1038 | B1 | 501-01 | DGP1015 | SER | DETECTION & EGRESS | N/A |  | R
KOR1043 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
KOR1045 | B1 | 803-01 | DGP1013 |  | DETECTION & EGRESS | PASS
KOR1046 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | DETECTION & EGRESS | N/A |  | R
KOR1047 | B1 | 830-01 | DGP1020 |  | DETECTION & EGRESS | PASS
KOR1051 | B1 | 652-02 | DGP1016 |  | DETECTION & EGRESS | PASS
KOR1052 | B1 | 611-02 | DGP1008 |  | DETECTION & EGRESS | N/A |  | R
KOR1053 | B1 | 650-01 | DGP1008 |  | DETECTION & EGRESS | PASS
KOR1054 | B1 | 650-02 | DGP1008 |  | DETECTION & EGRESS | PASS
KOR1055 | B1 | 611-01 | DGP1007 |  | DETECTION & EGRESS | N/A |  | R
KOR1056 | B1 | 640-04 | DGP1008 |  | DETECTION & EGRESS | PASS
KOR1057 | B1 | 640-03 | DGP1009 |  | DETECTION & EGRESS | PASS
KOR1058 | B1 | 830-03 | DGP1010 |  | DETECTION & EGRESS | PASS
KOR1059 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | DETECTION & EGRESS | N/A |  | R
KOR1060 | B1 | 803-02 | DGP1009 |  | DETECTION & EGRESS | FAIL | NOT REGISTERING IN FORCEFIELD
KOR1061 | B1 | 831-02 | DGP1010 |  | DETECTION & EGRESS | PASS
KOR1065 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
KOR1066 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
KOR1068 | B2 | 651-02 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
KOR1069 | B2 | 651-04 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
KOR1072 | B2 | 151-05 | DGP1019 |  | DETECTION & EGRESS | PASS
KOR1073 | B2 | 651-01 | DGP1018 |  | DETECTION & EGRESS | PASS
KOR1074 | B2 | 651-03 | DGP1018 |  | DETECTION & EGRESS | PASS
KOR1077 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1078 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1080 | LG | 239-01 | DGP1016 |  | DETECTION & EGRESS | PASS
KOR1082 | GF | S-09 | DGP1002 |  | DETECTION & EGRESS | N/A |  | R
KOR1083 | GF | 401-01 | DGP1003 |  | DETECTION & EGRESS | N/A |  | R
KOR1084 | GF | 405-02 | DGP1002 |  | DETECTION & EGRESS | N/A |  | R
KOR1101 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1102 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1103 | L1 | 710-03 | DGP1003 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1104 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
KOR1105 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1107 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1108 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1109 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1110 | L1 | 710-03 | DGP1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1111 | L1 | 710-03 | DGP1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1112 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1113 | L1 | 710-03 | DGP1003 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1114 | B1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1115 | B1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1116 | B1 | 709-2 | NAC1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1117 | GF | 650-03 | NAC1004 |  | DETECTION & EGRESS | PASS
KOR1118 | GF | 610-01 | DGP1004 | HV Substation 1 West | DETECTION & EGRESS | N/A | lock fails so fails,Possibly N/A or not installed
KOR1119 | GF | S-03 | DGP1005 | GF WEST ESC STAIRS 03 | DETECTION & EGRESS | PASS | Built into the ELL | 100% complete in ELM
KOR1120 | GF | 709-03 | NAC1005 |  | DETECTION & EGRESS | pass | Built into the ELL | 100% complete in ELM
KOR1121 | GF | 409-05 | NAC1005 |  | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1122 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% complete in ELM
KOR1123 | LG | S-07 | DGP1006 |  | DETECTION & EGRESS | N/A | Built into the ELL1023 - Faulty Lock
KOR1125 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1126 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1127 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1128 | B1 | 704-01 | DGP1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1130 | B1 | 704-01 | DGP1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1133 | B1 | 704-01 | DGP1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1134 | B1 | 704-01 | NAC1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1135 | B1 | 709-2 | DGP1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1136 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1137 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1138 | B1 | 709-2 | NAC1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1139 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1140 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1141 | B1 | 709-2 | DGP1010 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1142 | B1 | 709-2 | NAC1010 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1146 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
KOR1147 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
KOR1148 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
KOR1149 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
KOR1153 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
KOR1154 | B2 | 651-03 | DGP1018 | MDB-B B2 WEST | DETECTION & EGRESS | N/A |  | R
KOR1155 | B2 | 651-03 | DGP1018 | MDB-B B2 WEST | DETECTION & EGRESS | N/A |  | R
KOR1156 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1157 | B1 | 704-01 | DGP1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1158 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
KOR1159 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
KOR1160 | GF | 610-01 | NAC1004 |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
KOR1161 | GF | 610-02 | NAC1006 |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
KOR1162 | B1 | 704-01 | DGP1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1163 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1164 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1165 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1166 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1167 | B1 | 704-01 | NAC1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1168 | B1 | 704-01 | NAC1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1171 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1172 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1173 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
KOR1174 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
KOR1175 | B2 | 651-2 | NAC1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
KOR1176 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
KOR1180 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1181 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1182 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1183 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
KOR1184 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1186 | GF | 246-01 | NAC1005 | Loading Dock - West | DETECTION & EGRESS | N/A | Built into the ELL need key
KOR1187 | GF | 246-01 | NAC1005 | Loading Dock - West | DETECTION & EGRESS | N/A | Built into the ELL need key
KOR1190 | B1 | 704-01 | NAC1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
KOR1193 | B1 | 709-2 | NAC1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
KOR1196 | B1 | 704-01 | NAC1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
NAC1001 | L1 | 710-03 | NAC1001 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
NAC1002 | L1 | 710-03 | NAC1002 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
NAC1003 | L1 | 710-03 | NAC1003 |  | PANELS & CONTROLLERS | PASS | TAMPER OK, POWER OK,
NAC1004 | GF | 709-03 | NAC1004 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS | TAMPER K,MAINS K | 100% complete on ELM
NAC1005 | GF | 709-03 | NAC1005 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS |  | 100% complete on ELM
NAC1006 | GF | 709-03 | NAC1006 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS | TAMPER K,MAINS K | 100% complete on ELM
NAC1007 | B1 | 709-02 | NAC1007 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT
NAC1008 | B1 | 709-02 | NAC1008 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT
NAC1009 | B1 | 709-02 | NAC1009 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT
NAC1010 | B1 | 709-02 | NAC1010 |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT
NAC1011 | B1 | 704-01 | NAC1011 |  | PANELS & CONTROLLERS | PASS
NAC1012 | B1 | 704-01 | NAC1012 |  | PANELS & CONTROLLERS | PASS
NAC1013 | B1 | 704-01 | NAC1013 |  | PANELS & CONTROLLERS | PASS
NAC1014 | B1 | 704-01 | NAC1014 |  | PANELS & CONTROLLERS | PASS
NAC1015 | B1 | 704-01 | NAC1015 |  | PANELS & CONTROLLERS | PASS
NAC1016 | B2 | 651-02 | NAC1016 |  | PANELS & CONTROLLERS | PASS
NAC1017 | B2 | 651-02 | NAC1017 |  | PANELS & CONTROLLERS | PASS
NAC1018 | B2 | 651-03 | NAC1018 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
NAC1019 | B2 | 651-03 | NAC1019 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
NAC1020 | B2 | 651-03 | NAC1020 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS K
NAC1021 | B2 | 710-02 | NAC1021 |  | PANELS & CONTROLLERS | PASS | TAMPER K, POWER MAINS FAILURE K
PIR1001 | L2 | 803-03 | DGP1001 |  | DETECTION & EGRESS | PASS
PIR1002 | L2 | 811-04 | DGP1001 | HVAC PLANT ROOM L2 - EAST | DETECTION & EGRESS | FAIL | NO ACTIVITY REGISTERED | FAULTY
PIR1003 | L2 | 802-02 | DGP1001 |  | DETECTION & EGRESS | PASS
PIR1004 | L1 | S-05 | DGP1001 |  | DETECTION & EGRESS | PASS
PIR1005 | L1 | 710-03 | DGP1001 |  | DETECTION & EGRESS | PASS
PIR1006 | L2 | S-05 | DGP1001 |  | DETECTION & EGRESS | PASS
PIR1007 | L1 | 211-01 | DGP1001 | ICR L1 EAST | DETECTION & EGRESS | PASS
PIR1008 | L1 | 201-01 | DGP1002 | SCR L1 EAST | DETECTION & EGRESS | PASS
PIR1009 | L1 | 204-01 | DGP1002 | SMO L1 EAST | DETECTION & EGRESS | PASS
PIR1010 | GF | S-05 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1011 | GF | 306-01 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1012 | GF | 202-01 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1013 | GF | 246-01 | DGP1005 | GF - Loading bay - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1015 | LG | 234-02 | DGP1007 |  | DETECTION & EGRESS | PASS
PIR1016 | GF | 405-02 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1018 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1019 | GF | 610-01 | DGP1004 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1020 | GF | 610-02 | DGP1006 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1021 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1022 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1023 | GF | 709-03 | DGP1005 | COMMS CPB GF WEST | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1024 | GF | 409-05 | DGP1005 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1025 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1026 | GF | S-09 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1027 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | DETECTION & EGRESS | PASS
PIR1028 | LG | S-07 | DGP1006 | ESC STAIRS - LG - WEST | DETECTION & EGRESS | PASS
PIR1029 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | DETECTION & EGRESS | PASS
PIR1030 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | DETECTION & EGRESS | PASS
PIR1031 | B1 | 409-01 | DGP1011 | Fire Suppresion Room B1 - West | DETECTION & EGRESS | PASS
PIR1032 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | DETECTION & EGRESS | PASS
PIR1033 | B1 | 602-01 | DGP1012 |  | DETECTION & EGRESS | PASS
PIR1035 | B1 | 602-02 | DGP1012 |  | DETECTION & EGRESS | PASS
PIR1036 | B1 | 602-03 | DGP1011 |  | DETECTION & EGRESS | PASS
PIR1037 | B1 | 602-03 | DGP1011 |  | DETECTION & EGRESS | PASS
PIR1038 | B1 | 811-01 | DGP1012 |  | DETECTION & EGRESS | PASS
PIR1040 | B1 | 234-01 | DGP1014 |  | DETECTION & EGRESS | PASS
PIR1041 | B1 | 230-01 | DGP1014 |  | DETECTION & EGRESS | PASS
PIR1042 | B1 | 231-01 | DGP1014 |  | DETECTION & EGRESS | PASS
PIR1044 | B1 | 245-01 | DGP1015 |  | DETECTION & EGRESS | PASS
PIR1045 | B1 | 705-01 | DGP1015 |  | DETECTION & EGRESS | PASS
PIR1046 | B1 | 811-02 | DGP1015 |  | DETECTION & EGRESS | PASS
PIR1047 | B1 | 501-01 | DGP1015 | SER | DETECTION & EGRESS | PASS
PIR1049 | B1 | 704-01 | DGP1015 |  | DETECTION & EGRESS | PASS
PIR1051 | GF | 401-01 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1053 | B1 | S-03 | DGP1013 | ESC STAIRS - B1 WEST | DETECTION & EGRESS | PASS
PIR1054 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
PIR1055 | B1 | S-03 | DGP1013 | ESC STAIRS - B1 WEST | DETECTION & EGRESS | FAIL | COMING UP ON FF AS TAMPER ALARM
PIR1056 | B1 | 803-01 | DGP1013 |  | DETECTION & EGRESS | PASS
PIR1057 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | DETECTION & EGRESS | N/A |  | R
PIR1058 | B1 | 830-01 | DGP1020 |  | DETECTION & EGRESS | PASS
PIR1059 | B1 | S-04 | DGP1007 |  | DETECTION & EGRESS | PASS
PIR1061 | B1 | 652-02 | DGP1016 |  | DETECTION & EGRESS | PASS
PIR1062 | B1 | 611-02 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1063 | B1 | 650-01 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1064 | B1 | 650-02 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1065 | B1 | 611-01 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1066 | B1 | 640-04 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1067 | B1 | 640-03 | DGP1009 |  | DETECTION & EGRESS | PASS
PIR1068 | B1 | 409-04 | DGP1010 |  | DETECTION & EGRESS | PASS
PIR1069 | B1 | 830-03 | DGP1010 |  | DETECTION & EGRESS | PASS
PIR1070 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | DETECTION & EGRESS | N/A |  | R
PIR1071 | B1 | 803-02 | DGP1009 |  | DETECTION & EGRESS | FAIL | NOT REGISTERING IN FORCEFIELD, ISSUE WITH WIRING ?
PIR1072 | B1 | 831-02 | DGP1010 | OTE FAN ROM - B1 - WEST | DETECTION & EGRESS | INCOMPLETE | Access to be arranged to TVCS rooms
PIR1074 | B2 | 710-02 | DGP1021 |  | DETECTION & EGRESS | PASS
PIR1075 | B2 | S-04 | DGP1016 |  | DETECTION & EGRESS | PASS
PIR1076 | B2 | S-04 | DGP1021 |  | DETECTION & EGRESS | PASS
PIR1077 | B2 | 601-02 | DGP1017 |  | DETECTION & EGRESS | PASS
PIR1078 | B2 | 651-02 | DGP1017 |  | DETECTION & EGRESS | PASS
PIR1079 | B2 | 651-04 | DGP1017 |  | DETECTION & EGRESS | PASS
PIR1080 | B2 | 710-01 | DGP1021 |  | DETECTION & EGRESS | PASS
PIR1081 | B2 | 403-01 | DGP1019 |  | DETECTION & EGRESS | PASS
PIR1082 | B2 | 403-01 | DGP1019 |  | DETECTION & EGRESS | PASS
PIR1084 | B2 | 651-01 | DGP1018 |  | DETECTION & EGRESS | PASS
PIR1085 | B2 | 651-03 | DGP1018 |  | DETECTION & EGRESS | PASS | pir flashing amber, but showing on ff ok
PIR1086 | B2 | 409-03 | DGP1018 |  | DETECTION & EGRESS | PASS
PIR1087 | B2 | 601-01 | DGP1018 |  | DETECTION & EGRESS | PASS
PIR1088 | B2 | 601-01 | DGP1018 |  | DETECTION & EGRESS | PASS
PIR1089 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1090 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1091 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | DETECTION & EGRESS | PASS |  | 100% complete on ELM
PIR1092 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | DETECTION & EGRESS | PASS
PIR1093 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | DETECTION & EGRESS | PASS
PIR1094 | B1 | 602-01 | DGP1012 |  | DETECTION & EGRESS | PASS
PIR1095 | B1 | 602-02 | DGP1012 |  | DETECTION & EGRESS | PASS
PIR1096 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
PIR1097 | B1 | 650-01 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1098 | B1 | 640-04 | DGP1008 |  | DETECTION & EGRESS | PASS
PIR1099 | B1 | 640-03 | DGP1009 |  | DETECTION & EGRESS | PASS
PIR1100 | B1 | 831-02 | DGP1009 |  | DETECTION & EGRESS | FAIL | NOT REGISTERING ON FORCEFIELD
PIR1103 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
PIR1104 | B1 | 151-04 | DGP1007 |  | DETECTION & EGRESS | PASS
PIR1105 | B1 | 830-01 | DGP1020 |  | DETECTION & EGRESS | PASS
PIR1106 | LG | 239-01 | DGP1016 |  | DETECTION & EGRESS | PASS
PIR1107 | L1 | 205-01 |  |  | DETECTION & EGRESS | N/A |  | R
RAS1001 | L1 | 710-03 | NAC1001 | Field Dev Room - East L1 near SCR | ACCESS & ARMING | PASS | NO AREAS ASSIGNED THOUGH, NOT SURE IF IT NEEDS ANY AREA ASSIGNED
RAS1002 | GF | 650-04 | SMP1004 | LV Switch Room B2 - West | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1003 | GF | 650-03 | SMP1004 | LV Switch Room A2 - West | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1004 | GF | 610-01 | SMP1004 |  | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1005 | GF | 610-02 | SMP1004 |  | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1006 | GF | 706-01 | SMP1004 | Telephone Equipment Room - GF West | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1007 | B1 | 602-01 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1008 | B1 | 602-02 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1009 | B1 | 602-03 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1010 | B1 | 501-01 | SMP1002 | SER | ACCESS & ARMING | PASS
RAS1011 | B1 | 704-01 | SMP1011 |  | ACCESS & ARMING | PASS
RAS1012 | B1 | 611-02 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1013 | B1 | 650-01 | NAC1007 |  | ACCESS & ARMING | PASS
RAS1014 | B1 | 650-02 | NAC1007 |  | ACCESS & ARMING | PASS
RAS1015 | B1 | 611-01 | NAC1007 |  | ACCESS & ARMING | PASS | COVER BROKEN
RAS1016 | B2 | 601-01 | NAC1018 |  | ACCESS & ARMING | PASS
RAS1017 | B2 | 651-03 | NAC1018 |  | ACCESS & ARMING | PASS
RAS1018 | B2 | 651-01 | NAC1018 |  | ACCESS & ARMING | PASS
RAS1019 | B2 | 710-01 | NAC1018 |  | ACCESS & ARMING | PASS
RAS1020 | B2 | 710-02 | NAC1021 |  | ACCESS & ARMING | PASS
RAS1021 | B2 | 651-04 | SMP1005 |  | ACCESS & ARMING | PASS
RAS1022 | B2 | 651-02 | NAC1016 |  | ACCESS & ARMING | PASS
RAS1023 | B2 | 601-02 | SMP1005 |  | ACCESS & ARMING | PASS
RAS1024 | B1 | 705-01 | NAC1007 |  | ACCESS & ARMING | PASS
RAS1025 | GF | 409-05 | SMP1004 |  | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RAS1026 | LG | 802-01 | SMP1004 | Fire Suppresion Room LG - West | ACCESS & ARMING | PASS
RAS1027 | LG | 234-02 | NAC1007 | LG East - Equipment Room | ACCESS & ARMING | PASS
RAS1028 | B1 | 409-01 | SMP1002 | Fire Suppresion Room B1 - West | ACCESS & ARMING | PASS
RAS1029 | B1 | 652-01 | SMP1002 | TVS MCC ROOM A - West | ACCESS & ARMING | PASS
RAS1030 | B1 | 830-01 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1031 | B1 | 830-02 | SMP1002 | TVCS FAN ROOM - B1 - West | ACCESS & ARMING | N/A |  | R
RAS1032 | B1 | 803-01 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1033 | B1 | 831-01 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1034 | B1 | 234-01 | SMP1002 |  | ACCESS & ARMING | PASS
RAS1035 | B1 | 652-02 | NAC1007 |  | ACCESS & ARMING | PASS
RAS1036 | B1 | 409-04 | NAC1007 |  | ACCESS & ARMING | PASS | broken cover
RAS1037 | B1 | 831-02 | NAC1007 | OTE FAN ROM - B1 - WEST | ACCESS & ARMING | INCOMPLETE | SKIPPED at the start due to no access code, Access to be arranged to TVCS rooms
RAS1038 | B1 | 803-02 | NAC1007 | General Fan room - East | ACCESS & ARMING | INCOMPLETE | Access to be arranged to TVCS rooms
RAS1039 | B1 | 830-04 | NAC1007 | TVCS FAN ROOM - B1 - EAST | ACCESS & ARMING | N/A |  | R
RAS1040 | B1 | 830-03 | NAC1016 | TVCS FAN ROOM - B1 - EAST | ACCESS & ARMING | INCOMPLETE | SKIPPED at the start due to no access code, Access to be arranged to TVCS rooms
RAS1041 | L2 | 803-03 | NAC1001 |  | ACCESS & ARMING | PASS
RAS1042 | L2 | 802-02 | NAC1001 |  | ACCESS & ARMING | FAIL | SEE PHOTO - RAS SHOWS SYSTEM FAULT
RAS1043 | B1 | 704-01 | SMP1001 |  | ACCESS & ARMING | PASS | no areas to arm/disarm, but showing on ff anyway
RAS1044 | B1 | 704-01 | SMP1003 |  | ACCESS & ARMING | PASS
RAS1045 | GF | 709-03 | SMP1004 | COMMS CPB GF WEST | ACCESS & ARMING | PASS |  | 100% COMPLETE on ELM
RSW1001 | L2 | S-05 | DGP1001 |  | REED SWITCHES | PASS
RSW1002 | L2 | 803-03 | DGP1001 |  | REED SWITCHES | PASS
RSW1003 | L2 | 803-03 | DGP1001 |  | REED SWITCHES | PASS
RSW1004 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | REED SWITCHES | PASS
RSW1005 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | REED SWITCHES | PASS
RSW1008 | L2 | 811-04 | DGP1001 |  | REED SWITCHES | PASS
RSW1009 | L2 | 701-05 | DGP1003 |  | REED SWITCHES | FAIL | NEED CORRECT KEY ACCESS
RSW1011 | L1 | S-05 | DGP1001 |  | REED SWITCHES | PASS
RSW1019 | L1 | 709-06 | DGP1003 |  | REED SWITCHES | N/A |  | R
RSW1020 | L1 | 709-06 | DGP1003 |  | REED SWITCHES | N/A |  | R
RSW1023 | L1 | 709-06 | DGP1003 |  | REED SWITCHES | PASS
RSW1024 | L1 | 709-06 | DGP1003 |  | REED SWITCHES | PASS
RSW1025 | L1 | 211-01 | DGP1001 | ICR L1 EAST | REED SWITCHES | PASS
RSW1027 | L1 | 201-01 | DGP1002 | SCR L1 EAST | REED SWITCHES | PASS
RSW1029 | L1 | 701-05 | DGP1003 |  | REED SWITCHES | PASS
RSW1031 | L1 | 204-01 | DGP1002 | SMO L1 EAST | REED SWITCHES | PASS
RSW1032 | GF | S-05 | DGP1002 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1033 | GF | 151-12 | DGP1002 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1034 | GF | 151-12 | DGP1002 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1035 | GF | 306-01 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1036 | GF | 202-01 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1038 | GF | 701-04 | DGP1002 | COMMS RISER GF East | REED SWITCHES | FAIL | NO ACCESS - Door is between the Arches See drawing AEN_L1319
RSW1039 | GF | 701-05 | DGP1002 |  | REED SWITCHES | PASS
RSW1040 | GF | 701-03 | DGP1002 | COMMS RISER GF East | REED SWITCHES | FAIL | NO ACCESS - Door is between the Arches See drawing AEN_L1319
RSW1042 | LG | 701-03 | DGP1007 |  | REED SWITCHES | FAIL | NEED KEY
RSW1043 | LG | 701-04 | DGP1007 |  | REED SWITCHES | FAIL | NEED KEY
RSW1047 | LG | 701-05 | DGP1007 |  | REED SWITCHES | PASS
RSW1051 | LG | 812-02 | DGP1007 |  | REED SWITCHES | PASS
RSW1052 | LG | 812-02 | DGP1007 |  | REED SWITCHES | PASS
RSW1053 | LG | 812-02 | DGP1007 |  | REED SWITCHES | PASS
RSW1054 | LG | 812-02 | DGP1007 |  | REED SWITCHES | PASS
RSW1058 | GF | 246-01 | DGP1005 | GF - Loading bay - West | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1059 | GF | 246-01 | DGP1005 | GF - Loading bay - West | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1060 | GF | 246-01 | DGP1005 | GF - Loading bay - West | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1061 | GF | 246-01 | DGP1005 | GF - Loading bay - West | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1062 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1063 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | REED SWITCHES | FAIL | NOT REGISTERING IN FF
RSW1064 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1065 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | REED SWITCHES | FAIL | NOT REGISTERING IN FF
RSW1066 | GF | 701-02 | DGP1006 | COMMS RISER GF WEST | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1067 | GF | 701-01 | DGP1006 | COMMS RISER GF WEST | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1068 | GF | S-03 | DGP1005 | ESC STAIRS - GF - WEST | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1073 | LG | 701-01 | DGP1006 | COMMS RISER LG WEST | REED SWITCHES | PASS
RSW1074 | LG | 701-02 | DGP1006 | COMMS RISER LG WEST | REED SWITCHES | PASS
RSW1079 | LG | S-07 | DGP1006 | ESC STAIRS - LG - WEST | REED SWITCHES | PASS
RSW1080 | LG | 239-01 | DGP1016 |  | REED SWITCHES | PASS
RSW1081 | LG | 239-01 | DGP1016 |  | REED SWITCHES | PASS
RSW1102 | B1 | 811-01 | DGP1012 |  | REED SWITCHES | PASS
RSW1103 | B1 | 230-01 | DGP1014 |  | REED SWITCHES | PASS
RSW1104 | B1 | 230-01 | DGP1014 |  | REED SWITCHES | FAIL | not showing on ff
RSW1105 | B1 | 231-01 | DGP1014 |  | REED SWITCHES | PASS
RSW1106 | B1 | 231-01 | DGP1014 |  | REED SWITCHES | PASS
RSW1107 | B1 | 151-10 | DGP1014 |  | REED SWITCHES | PASS
RSW1108 | B1 | 151-10 | DGP1014 |  | REED SWITCHES | FAIL | not showing on ff
RSW1109 | B1 | 151-09 | DGP1015 |  | REED SWITCHES | PASS
RSW1110 | B1 | 151-09 | DGP1015 |  | REED SWITCHES | PASS
RSW1112 | B1 | 245-01 | DGP1015 |  | REED SWITCHES | PASS
RSW1115 | B1 | 811-02 | DGP1015 |  | REED SWITCHES | PASS
RSW1127 | B1 | 709-04 | SMP1001 |  | REED SWITCHES | PASS
RSW1128 | B1 | 709-04 | SMP1001 |  | REED SWITCHES | PASS
RSW1129 | GF | 401-01 | DGP1003 |  | REED SWITCHES | N/A |  | R
RSW1138 | B1 | 701-02 | SMP1001 | COMMS RISER B1 WEST | REED SWITCHES | PASS
RSW1139 | B1 | 701-01 | SMP1001 | COMMS RISER B1 WEST | REED SWITCHES | PASS
RSW1144 | B1 | S-03 | DGP1013 | ESC STAIRS - B1 WEST | REED SWITCHES | PASS
RSW1145 | B1 | S-03 | DGP1013 | ESC STAIRS - B1 WEST | REED SWITCHES | PASS
RSW1146 | B1 | S-03 | DGP1013 | ESC STAIRS - B1 WEST | REED SWITCHES | PASS
RSW1151 | GF | 246-02 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1152 | GF | 246-02 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1153 | GF | 246-02 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1154 | GF | 246-02 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1159 | B1 | 151-04 | DGP1007 | EAST - BOH CORRIDOR 04 | REED SWITCHES | PASS
RSW1160 | B1 | 151-04 | DGP1007 | EAST - BOH CORRIDOR 04 | REED SWITCHES | PASS
RSW1161 | B1 | S-04 | DGP1007 |  | REED SWITCHES | PASS
RSW1164 | B1 | 701-03 | DGP1007 |  | REED SWITCHES | PASS
RSW1165 | B1 | 701-04 | DGP1007 |  | REED SWITCHES | PASS
RSW1166 | B1 | 709-02 | DGP1010 |  | REED SWITCHES | PASS
RSW1167 | B1 | 709-02 | DGP1010 |  | REED SWITCHES | PASS
RSW1168 | B1 | 709-02 | DGP1010 |  | REED SWITCHES | PASS
RSW1169 | B1 | 709-02 | DGP1010 |  | REED SWITCHES | PASS
RSW1210 | B2 | S-04 | DGP1016 |  | REED SWITCHES | PASS
RSW1211 | B2 | S-04 | DGP1016 |  | REED SWITCHES | PASS
RSW1212 | B2 | S-04 | DGP1021 |  | REED SWITCHES | PASS
RSW1213 | B2 | S-04 | DGP1021 |  | REED SWITCHES | PASS
RSW1214 | B2 | S-04 | DGP1021 |  | REED SWITCHES | PASS
RSW1215 | B2 | 151-15 | DGP1017 |  | REED SWITCHES | PASS
RSW1216 | B2 | 151-16 | DGP1016 |  | REED SWITCHES | PASS
RSW1217 | B2 | 151-16 | DGP1016 |  | REED SWITCHES | PASS
RSW1218 | B2 | 151-16 | DGP1016 |  | REED SWITCHES | FAIL | NO ALARMS IN FF
RSW1219 | B2 | 151-16 | DGP1016 |  | REED SWITCHES | FAIL | no status on forcefield
RSW1220 | B2 | 151-15 | DGP1017 |  | REED SWITCHES | PASS
RSW1221 | B2 | 701-03 | DGP1016 |  | REED SWITCHES | FAIL | Not registering on FF
RSW1222 | B2 | 701-04 | DGP1016 |  | REED SWITCHES | FAIL | not registering on FF
RSW1223 | GF | 401-01 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete on ELM
RSW1226 | B2 | 414-01 | DGP1017 | MFB RNERV | REED SWITCHES | FAIL | Track Access to be arranged
RSW1231 | B2 | 403-01 | DGP1019 |  | REED SWITCHES | PASS
RSW1232 | B2 | 403-01 | DGP1019 |  | REED SWITCHES | FAIL | not registering on ff
RSW1233 | B2 | 403-01 | DGP1019 |  | REED SWITCHES | PASS
RSW1234 | B2 | 403-01 | DGP1019 |  | REED SWITCHES | PASS
RSW1235 | B2 | 403-01 | DGP1019 |  | REED SWITCHES | PASS
RSW1236 | B2 | 701-02 | DGP1018 |  | REED SWITCHES | PASS | doors labelled as HV, should be Comms, see photos
RSW1237 | B2 | 701-01 | DGP1018 |  | REED SWITCHES | PASS | doors labelled as HV, should be Comms, see photos
RSW1238 | B2 | 151-07 | DGP1018 |  | REED SWITCHES | PASS
RSW1243 | B2 | 151-07 | DGP1018 |  | REED SWITCHES | PASS
RSW1244 | B2 | 151-05 | DGP1019 |  | REED SWITCHES | PASS
RSW1245 | B2 | 151-05 | DGP1019 |  | REED SWITCHES | PASS
RSW1246 | B2 | 414-02 | DGP1019 | MFB RNERV | REED SWITCHES | FAIL | Track Access to be arranged
RSW1247 | L1 | 211-01 | DGP1001 | ICR L1 EAST | REED SWITCHES | PASS
RSW1250 | B1 | 151-04 | DGP1007 | EAST - BOH CORRIDOR 04 | REED SWITCHES | PASS
RSW1251 | B1 | 151-04 | DGP1007 | EAST - BOH CORRIDOR 04 | REED SWITCHES | PASS
RTB1001 | L1 | 710-03 | DGP1001 |  | REED SWITCHES | PASS
RTB1002 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1003 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1004 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1005 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1006 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1007 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1008 | GF | 610-01 | DGP1004 |  | REED SWITCHES | PASS |  | ELM 100% complete
RTB1009 | GF | 610-01 | DGP1004 |  | REED SWITCHES | PASS | damage to hinge prevent door closing fully | ELM 100% complete
RTB1010 | GF | 610-01 | DGP1004 |  | REED SWITCHES | PASS |  | ELM 100% complete
RTB1011 | GF | 610-02 | DGP1006 |  | REED SWITCHES | PASS |  | ELM 100% complete
RTB1012 | GF | 610-02 | DGP1006 |  | REED SWITCHES | PASS |  | ELM 100% complete
RTB1013 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1014 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | REED SWITCHES | PASS |  | ELM 100% complete
RTB1015 | GF | 409-05 | DGP1005 |  | REED SWITCHES | PASS |  | ELM 100% complete
RTB1016 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | REED SWITCHES | PASS
RTB1017 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | REED SWITCHES | PASS
RTB1018 | LG | 234-02 | DGP1007 |  | REED SWITCHES | PASS
RTB1021 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | REED SWITCHES | PASS
RTB1022 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | REED SWITCHES | PASS
RTB1023 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | REED SWITCHES | PASS
RTB1024 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | REED SWITCHES | PASS
RTB1025 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | REED SWITCHES | PASS
RTB1026 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | REED SWITCHES | PASS
RTB1027 | B1 | 409-01 | DGP1011 | Fire Suppresion Room B1 - West | REED SWITCHES | PASS
RTB1028 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | REED SWITCHES | PASS
RTB1029 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | REED SWITCHES | PASS
RTB1030 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | REED SWITCHES | PASS
RTB1031 | B1 | 602-01 | DGP1012 |  | REED SWITCHES | PASS
RTB1032 | B1 | 602-01 | DGP1012 |  | REED SWITCHES | PASS
RTB1033 | B1 | 602-01 | DGP1012 |  | REED SWITCHES | PASS
RTB1034 | B1 | 602-01 | DGP1012 |  | REED SWITCHES | PASS
RTB1035 | B1 | 831-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1036 | B1 | 831-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1037 | B1 | 831-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1038 | B1 | 803-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1039 | B1 | 803-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1040 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | REED SWITCHES | N/A |  | R
RTB1041 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | REED SWITCHES | N/A |  | R
RTB1042 | B1 | 830-01 | DGP1020 |  | REED SWITCHES | PASS
RTB1043 | B1 | 830-01 | DGP1020 |  | REED SWITCHES | PASS
RTB1044 | B1 | 602-02 | DGP1012 |  | REED SWITCHES | PASS
RTB1045 | B1 | 602-02 | DGP1012 |  | REED SWITCHES | PASS
RTB1046 | B1 | 602-02 | DGP1012 |  | REED SWITCHES | PASS
RTB1047 | B1 | 602-02 | DGP1012 |  | REED SWITCHES | PASS
RTB1048 | B1 | 602-03 | DGP1011 |  | REED SWITCHES | PASS
RTB1049 | B1 | 602-03 | DGP1011 |  | REED SWITCHES | PASS
RTB1050 | B1 | 602-03 | DGP1011 |  | REED SWITCHES | PASS
RTB1051 | B1 | 602-03 | DGP1011 |  | REED SWITCHES | PASS
RTB1052 | B1 | 234-01 | DGP1014 |  | REED SWITCHES | PASS
RTB1053 | B1 | 234-01 | DGP1014 |  | REED SWITCHES | PASS
RTB1054 | B1 | 705-01 | DGP1015 |  | REED SWITCHES | PASS
RTB1055 | B1 | 705-01 | DGP1015 |  | REED SWITCHES | PASS
RTB1056 | B1 | 501-01 | DGP1015 | SER | REED SWITCHES | PASS
RTB1057 | B1 | 501-01 | DGP1015 | SER | REED SWITCHES | PASS
RTB1058 | B1 | 704-01 | DGP1015 |  | REED SWITCHES | PASS
RTB1059 | B1 | 704-01 | DGP1015 |  | REED SWITCHES | PASS
RTB1060 | B1 | 611-02 | DGP1008 |  | REED SWITCHES | PASS
RTB1061 | B1 | 611-02 | DGP1008 |  | REED SWITCHES | PASS
RTB1062 | B1 | 650-01 | DGP1008 |  | REED SWITCHES | PASS
RTB1063 | B1 | 650-01 | DGP1008 |  | REED SWITCHES | PASS
RTB1064 | B1 | 650-01 | DGP1008 |  | REED SWITCHES | PASS
RTB1065 | B1 | 650-02 | DGP1008 |  | REED SWITCHES | PASS
RTB1066 | B1 | 650-02 | DGP1008 |  | REED SWITCHES | PASS
RTB1067 | B1 | 650-02 | DGP1008 |  | REED SWITCHES | PASS
RTB1068 | B1 | 611-01 | DGP1009 |  | REED SWITCHES | PASS
RTB1069 | B1 | 611-01 | DGP1009 |  | REED SWITCHES | PASS
RTB1070 | B1 | 611-01 | DGP1009 |  | REED SWITCHES | PASS
RTB1071 | B1 | 640-04 | DGP1008 |  | REED SWITCHES | PASS
RTB1072 | B1 | 640-04 | DGP1008 |  | REED SWITCHES | PASS
RTB1073 | B1 | 640-04 | DGP1008 |  | REED SWITCHES | PASS
RTB1074 | B1 | 640-03 | DGP1009 |  | REED SWITCHES | PASS
RTB1075 | B1 | 640-03 | DGP1009 |  | REED SWITCHES | PASS
RTB1076 | B1 | 640-03 | DGP1009 |  | REED SWITCHES | PASS
RTB1077 | B1 | 409-04 | DGP1010 |  | REED SWITCHES | PASS
RTB1078 | B1 | 652-02 | DGP1009 |  | REED SWITCHES | PASS
RTB1080 | B1 | 652-02 | DGP1016 |  | REED SWITCHES | PASS
RTB1081 | B1 | 652-02 | DGP1016 |  | REED SWITCHES | PASS
RTB1082 | B2 | 409-03 | DGP1018 |  | REED SWITCHES | PASS
RTB1083 | B2 | 601-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1084 | B2 | 601-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1085 | B2 | 601-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1086 | B2 | 601-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1087 | B2 | 651-03 | DGP1018 |  | REED SWITCHES | PASS
RTB1088 | B2 | 651-03 | DGP1018 |  | REED SWITCHES | PASS
RTB1089 | B2 | 651-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1090 | B2 | 651-01 | DGP1018 |  | REED SWITCHES | PASS
RTB1091 | B2 | 710-01 | DGP1021 |  | REED SWITCHES | PASS
RTB1092 | B2 | 710-02 | DGP1021 |  | REED SWITCHES | PASS
RTB1095 | B2 | 651-04 | DGP1017 |  | REED SWITCHES | PASS
RTB1096 | B2 | 651-04 | DGP1017 |  | REED SWITCHES | PASS
RTB1097 | B2 | 651-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1098 | B2 | 651-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1099 | B2 | 409-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1100 | B2 | 601-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1101 | B2 | 601-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1102 | B2 | 601-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1103 | B2 | 601-02 | DGP1017 |  | REED SWITCHES | PASS
RTB1104 | B1 | 831-02 | DGP1010 |  | REED SWITCHES | PASS | TESTING NOW…
RTB1105 | B1 | 830-03 | DGP1010 |  | REED SWITCHES | PASS
RTB1106 | B1 | 830-03 | DGP1010 |  | REED SWITCHES | PASS
RTB1107 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | REED SWITCHES | N/A |  | R
RTB1108 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | REED SWITCHES | N/A |  | R
RTB1109 | B1 | 803-02 | DGP1009 |  | REED SWITCHES | PASS
RTB1110 | B1 | 803-02 | DGP1009 |  | REED SWITCHES | PASS
RTB1111 | B1 | 831-02 | DGP1010 |  | REED SWITCHES | PASS
RTB1112 | B1 | 831-02 | DGP1010 |  | REED SWITCHES | PASS
RTB1113 | L2 | 802-02 | DGP1001 |  | REED SWITCHES | PASS
RTB1114 | L2 | 802-02 | DGP1001 |  | REED SWITCHES | PASS
RTB1115 | B1 | 831-01 | DGP1013 |  | REED SWITCHES | PASS
RTB1116 | B1 | 831-02 | DGP1005 |  | REED SWITCHES | PASS
RTB1117 | B1 | 831-02 | DGP1009 |  | REED SWITCHES | PASS
RTB1120 | B1 | 830-01 | DGP1020 |  | REED SWITCHES | PASS
RTB1121 | B1 | 830-01 | DGP1020 |  | REED SWITCHES | N/A |  | R
RTB1122 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | REED SWITCHES | N/A |  | R
RTB1123 | GF | 709-03 | DGP1005 | COMMS CPB GF WEST | REED SWITCHES | PASS |  | ELM 100% complete
RTB1124 | B1 | 830-03 | DGP1007 | TVCS FAN ROOM - B1 - EAST | REED SWITCHES | N/A |  | R
RTB1125 | B1 | 830-04 | DGP1007 | TVCS FAN ROOM - B1 - EAST | REED SWITCHES | N/A |  | R
RTE1001 | L2 | 803-03 | DGP1001 |  | DETECTION & EGRESS | PASS
RTE1002 | GF | 811-03 | DGP1006 | HVAC PLANT - GF - WEST | DETECTION & EGRESS | PASS |  | not in the execution list
RTE1003 | L2 | 802-02 | DGP1001 |  | DETECTION & EGRESS | N/A |  | R
RTE1006 | GF | 151-12 | DGP1002 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1009 | LG | 812-02 | DGP1007 |  | DETECTION & EGRESS | PASS
RTE1010 | LG | 812-02 | DGP1007 |  | DETECTION & EGRESS | PASS
RTE1011 | GF | 650-03 | DGP1004 | LV Switch Room A2 - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1018 | GF | 706-01 | DGP1006 | Telephone Equipment Room - GF West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1019 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1021 | LG | 802-01 | DGP1006 | Fire Suppresion Room LG - West | DETECTION & EGRESS | PASS
RTE1022 | B1 | 640-01 | DGP1019 | UBS Battery Room A - West | DETECTION & EGRESS | PASS
RTE1023 | B1 | 640-02 | DGP1011 | UBS Battery Room B - West | DETECTION & EGRESS | PASS
RTE1024 | B1 | 652-01 | DGP1011 | TVS MCC ROOM A - West | DETECTION & EGRESS | PASS
RTE1031 | B1 | 234-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
RTE1032 | B1 | 230-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
RTE1033 | B1 | 231-01 | DGP1014 |  | DETECTION & EGRESS | N/A |  | R
RTE1035 | B1 | 151-09 | DGP1015 |  | DETECTION & EGRESS | PASS
RTE1036 | B1 | 705-01 | DGP1015 |  | DETECTION & EGRESS | N/A |  | R
RTE1038 | B1 | 501-01 | DGP1015 | SER | DETECTION & EGRESS | N/A |  | R
RTE1043 | B1 | 831-01 | DGP1013 |  | DETECTION & EGRESS | PASS
RTE1045 | B1 | 803-01 | DGP1013 |  | DETECTION & EGRESS | PASS
RTE1046 | B1 | 830-02 | DGP1020 | TVCS FAN ROOM - B1 - West | DETECTION & EGRESS | N/A |  | R
RTE1047 | B1 | 830-01 | DGP1020 |  | DETECTION & EGRESS | PASS
RTE1051 | B1 | 652-02 | DGP1016 |  | DETECTION & EGRESS | PASS
RTE1052 | B1 | 611-02 | DGP1008 |  | DETECTION & EGRESS | N/A |  | R
RTE1053 | B1 | 650-01 | DGP1008 |  | DETECTION & EGRESS | PASS
RTE1054 | B1 | 650-02 | DGP1008 |  | DETECTION & EGRESS | PASS
RTE1055 | B1 | 611-01 | DGP1007 |  | DETECTION & EGRESS | N/A |  | R
RTE1056 | B1 | 640-04 | DGP1008 |  | DETECTION & EGRESS | PASS
RTE1057 | B1 | 640-03 | DGP1009 |  | DETECTION & EGRESS | PASS
RTE1058 | B1 | 830-03 | DGP1010 |  | DETECTION & EGRESS | PASS
RTE1059 | B1 | 830-04 | DGP1010 | TVCS FAN ROOM - B1 - EAST | DETECTION & EGRESS | N/A |  | R
RTE1060 | B1 | 803-02 | DGP1009 |  | DETECTION & EGRESS | FAIL | NOT REGISTERING IN FORCEFIELD
RTE1061 | B1 | 831-02 | DGP1010 |  | DETECTION & EGRESS | PASS
RTE1065 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
RTE1066 | B2 | 151-16 | DGP1016 |  | DETECTION & EGRESS | PASS
RTE1068 | B2 | 651-02 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
RTE1069 | B2 | 651-04 | DGP1017 |  | DETECTION & EGRESS | N/A |  | R
RTE1072 | B2 | 151-05 | DGP1019 |  | DETECTION & EGRESS | PASS
RTE1073 | B2 | 651-01 | DGP1018 |  | DETECTION & EGRESS | PASS
RTE1074 | B2 | 651-03 | DGP1018 |  | DETECTION & EGRESS | PASS
RTE1077 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1078 | GF | 246-02 | DGP1003 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1080 | LG | 239-01 | DGP1016 |  | DETECTION & EGRESS | PASS
RTE1082 | GF | S-09 | DGP1002 |  | DETECTION & EGRESS | N/A |  | R
RTE1083 | GF | 401-01 | DGP1003 |  | DETECTION & EGRESS | N/A |  | R
RTE1084 | GF | 405-02 | DGP1002 |  | DETECTION & EGRESS | N/A | PUSHBAR | R
RTE1101 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | Not Found
RTE1102 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1103 | L1 | 710-03 | DGP1003 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1104 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
RTE1105 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1107 | L1 | 710-03 | DGP1001 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1108 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1109 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1110 | L1 | 710-03 | DGP1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1111 | L1 | 710-03 | DGP1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1112 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
RTE1113 | L1 | 710-03 | DGP1003 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1114 | B1 |  |  |  | DETECTION & EGRESS | N/A |  | Not Found
RTE1115 | B1 |  |  |  | DETECTION & EGRESS | N/A |  | Not Found
RTE1116 | B1 | 709-2 | NAC1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1117 | GF | 650-03 | NAC1004 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1118 | GF | 610-01 | DGP1004 | HV Substation 1 West | DETECTION & EGRESS | N/A | lock fails so fails,Possibly N/A or not installed
RTE1119 | GF | S-03 | DGP1005 | GF WEST ESC STAIRS 03 | DETECTION & EGRESS | PASS | Built into the ELL | 100% complete on ELM
RTE1120 | GF | 709-03 | NAC1005 |  | DETECTION & EGRESS | PASS | Built into the ELL | 100% complete on ELM
RTE1121 | GF | 409-05 | NAC1005 |  | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1122 | GF | 650-04 | DGP1004 | LV Switch Room B2 - West | DETECTION & EGRESS | PASS |  | 100% complete on ELM
RTE1123 | LG | S-07 | DGP1006 |  | DETECTION & EGRESS | N/A | Built into the ELL1023 - Faulty Lock
RTE1125 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1126 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1127 | B1 | 704-01 | DGP1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1128 | B1 | 704-01 | DGP1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1130 | B1 | 704-01 | DGP1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1133 | B1 | 704-01 | DGP1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1134 | B1 | 704-01 | NAC1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1135 | B1 | 709-2 | DGP1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1136 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1137 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1138 | B1 | 709-2 | NAC1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1139 | B1 | 709-2 | DGP1008 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1140 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1141 | B1 | 709-2 | DGP1010 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1142 | B1 | 709-2 | NAC1010 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1146 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
RTE1147 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
RTE1148 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
RTE1149 | B2 | 651-2 | DGP1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
RTE1153 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
RTE1154 | B2 | 651-03 | DGP1018 | MDB-B B2 WEST | DETECTION & EGRESS | N/A |  | R
RTE1155 | B2 | 651-03 | DGP1018 | MDB-B B2 WEST | DETECTION & EGRESS | N/A |  | R
RTE1156 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
RTE1157 | B1 | 704-01 | DGP1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1158 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
RTE1159 | B2 |  |  |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
RTE1160 | GF | 610-01 | NAC1004 |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
RTE1161 | GF | 610-02 | NAC1006 |  | DETECTION & EGRESS | N/A | Unable to find in drawings | R
RTE1162 | B1 | 704-01 | DGP1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1163 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1164 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1165 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1166 | B1 | 704-01 | NAC1012 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1167 | B1 | 704-01 | NAC1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1168 | B1 | 704-01 | NAC1011 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1171 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1172 | B1 | 709-2 | DGP1009 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1173 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
RTE1174 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
RTE1175 | B2 | 651-2 | NAC1017 | MDB-A B2 EAST | DETECTION & EGRESS | N/A |  | R
RTE1176 | B2 |  |  |  | DETECTION & EGRESS | N/A | NOT found in drawings | R
RTE1180 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
RTE1181 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1182 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1183 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
RTE1184 | L1 | 710-03 | NAC1002 | FDR L1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1186 | GF | 246-01 | NAC1005 | Loading Dock - West | DETECTION & EGRESS | N/A | Built into the ELL need key
RTE1187 | GF | 246-01 | NAC1005 | Loading Dock - West | DETECTION & EGRESS | N/A | Built into the ELL need key
RTE1190 | B1 | 704-01 | NAC1013 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RTE1193 | B1 | 709-2 | NAC1007 | COMMS CPB B1 EAST | DETECTION & EGRESS | N/A |  | R
RTE1196 | B1 | 704-01 | NAC1015 | CER B1 WEST | DETECTION & EGRESS | N/A |  | R
RWG1001 | GF | 102-01 | DGP1002 |  | REED SWITCHES | PASS |  | 100% complete in ELM
RWG1002 | GF | 102-01 | DGP1002 |  | REED SWITCHES | PASS |  | 100% complete in ELM
RWG1003 | GF | 202-01 |  |  | REED SWITCHES | N/A | REMOVED FROM DESIGN | R
RWG1004 | GF | 202-01 | DGP1003 |  | REED SWITCHES | PASS |  | 100% complete in ELM
RWG1005 | B2 | 413-01 | DGP1019 | MFB RNERV - B2 West | REED SWITCHES | FAIL | Track Access to be arranged
RWG1006 | B2 | 413-01 | DGP1019 | MFB RNERV - B2 West | REED SWITCHES | FAIL | Track Access to be arranged
RWG1007 | B2 | 413-02 | DGP1017 | MFB RNERV | REED SWITCHES | FAIL | Track Access to be arranged
RWG1008 | B2 | 413-02 | DGP1017 | MFB RNERV | REED SWITCHES | FAIL | Track Access to be arranged
RWG1009 | B2 | 413-02 | DGP1017 | MFB RNERV | REED SWITCHES | FAIL | Track Access to be arranged
RWG1010 | B2 | 413-01 | DGP1019 | MFB RNERV - B2 West | REED SWITCHES | FAIL | Track Access to be arranged
RWG1126 | GF | 405-02 | DGP1002 |  | REED SWITCHES | PASS |  | not in execution list
RWG1127 | GF | 405-02 | DGP1002 |  | REED SWITCHES | PASS |  | not in execution list
RWG1128 | GF | S-09 | DGP1002 |  | REED SWITCHES | PASS |  | not in execution list
RWG1129 | GF | 401-01 |  |  | REED SWITCHES | PASS |  | not in execution list
RWG1130 | GF | S-09 | DGP1002 |  | REED SWITCHES | PASS |  | not in execution list
SMP1001 | B1 | 704-01 | SMP1001 |  | PANELS & CONTROLLERS | PASS
SMP1002 | B1 | 704-01 | SMP1002 |  | PANELS & CONTROLLERS | PASS
SMP1003 | B1 | 704-01 | SMP1003 |  | PANELS & CONTROLLERS | PASS | tamper ok
SMP1004 | GF | 709-03 | SMP1004 | COMMS CPB GF WEST | PANELS & CONTROLLERS | PASS
SMP1005 | B2 | 651-02 | SMP1005 |  | PANELS & CONTROLLERS | PASS | TAMPER K,
SMP1006 | B2 | 651-03 | SMP1006 |  | PANELS & CONTROLLERS | PASS | TAMPER K, MAINS OK
SMP1007 | B1 | 709-02 |  |  | PANELS & CONTROLLERS | PASS | TAMPER CORRECT ON FF, MAINS FAIL CORRECT
TSW1001 & TSW1002 | B1 | 704-01 | OCS01 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1003 & TSW1004 | B1 | 704-01 | OCS02 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1005 & TSW1006 | B1 | 704-01 | OCS03 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1007 & TSW1008 | B1 | 704-01 | OCS04 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1009 & TSW1010 | B1 | 704-01 | OCS05 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1011 & TSW1012 | B1 | 704-01 | OCS06 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1013 & TSW1014 | B1 | 704-01 | OCS07 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1015 & TSW1016 | B1 | 704-01 | OCS08 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1017 & TSW1018 | B1 | 704-01 | ICT01 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1019 & TSW1020 | B1 | 704-01 | FTP01 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1021 & TSW1022 | B1 | 704-01 | FTP02 | CER B1 WEST | REED SWITCHES | FAIL | 1 DOOR NOT COMING UP IN FF | only one side tamper working - TSW1022
TSW1023 & TSW1024 | B1 | 704-01 | CMS01 | CER B1 WEST | REED SWITCHES | PASS | 2 doors
TSW1025 & TSW1026 | B1 | 704-01 | SCADA-01 | CER B1 WEST | REED SWITCHES | FAIL | cannot test Rack Door Lock Tagged out by MTM ELECTROL SCADA TECHS | cannot test Rack Door Lock Tagged out
TSW1027 & TSW1028 | L1 | 710-03 | OCS09 | FDR L1 EAST | REED SWITCHES | PASS
TSW1030 & TSW1029 | L1 | 709-06 | OCS10 | COMMS CPB L1 EAST | REED SWITCHES | PASS
TSW1032 & TSW1031 | L1 | 709-06 | ICT02 | COMMS CPB L1 EAST | REED SWITCHES | PASS
TSW1034 & TSW1033 | GF | 306-1 | OCS13 | MYKI ROOM GF EAST | REED SWITCHES | PASS |  | not in the execution list
TSW1038 & TSW1037 | GF | 709-03 | OCS11 | COMMS CPB GF WEST | REED SWITCHES | PASS |  | 100% complete on ELM
TSW1040 & TSW1039 | GF | 709-03 | ICT03 | COMMS CPB GF WEST | REED SWITCHES | PASS |  | 100% complete on ELM
TSW1042 & TSW1041 | B1 | 812-2 | OCS14 | LG EAST | REED SWITCHES | PASS
TSW1044 & TSW1043 | B1 | 709-02 | OCS15 | COMMS CPB B1 EAST | REED SWITCHES | Pass
TSW1045 & TSW1046 | B2 | 651-03 | OCS16 | MDB-B B2 WEST | REED SWITCHES | FAIL | NOT REGISTERING ON FF
TSW1047 & TSW1048 | B2 | 651-03 | PFTP01 | MDB-B B2 WEST | REED SWITCHES | FAIL | NOT REGISTERING ON FF
TSW1049 & TSW1050 | B2 | 710-01 | OCS17 |  | REED SWITCHES | PASS
TSW1051 & TSW1052 | B2 | 710-02 | OCS18 |  | REED SWITCHES | PASS
TSW1053 & TSW1054 | B2 | 651-2 | OCS19 | MDB-A B2 EAST | REED SWITCHES | PASS
TSW1055 & TSW1056 | B2 | 651-2 | PFTP02 | MDB-A B2 EAST | REED SWITCHES | FAIL | CANNOT TEST RACK DOOR LOCKED, NEED KEY
TSW1062 & TSW1061 | GF |  |  |  | REED SWITCHES | N/A |  | R
TSW1064 & TSW1063 | GF |  |  |  | REED SWITCHES | N/A |  | R
TSW1066 & TSW1065 | GF |  |  |  | REED SWITCHES | N/A |  | R
TSW1067 & TSW1068 | GF | 706-01 | FTP01 | Telephone Equipment Room - GF West | REED SWITCHES | PASS |  | 100% complete on ELM
TSW1070 & TSW1069 | GF | 706-01 | FTP02 | Telephone Equipment Room - GF West | REED SWITCHES | PASS |  | 100% complete on ELM
TSW1071 | LG | 151-14 |  | LG WEST | REED SWITCHES | FAIL | No key to open
TSW1072 | LG | 151-14 |  | LG WEST | REED SWITCHES | FAIL | No key to open
TSW1073 | B1 | 701-1 |  | COMMS RISER LG WEST | REED SWITCHES | FAIL | No tamper switch installed (see photo)
TSW1074 | B1 | 701-2 |  | COMMS RISER LG WEST | REED SWITCHES | FAIL | No tamper switch installed (see photo)
TSW1075 | B2 | 151-05 |  |  | REED SWITCHES | FAIL | no tamper installed
TSW1076 | B2 | 151-05 |  |  | REED SWITCHES | FAIL | no tamper installed
TSW1077 | B1 | 151-6 |  | BOH CORRIDOR B2 EAST | REED SWITCHES | FAIL | No tamper switch installed (see photo)
TSW1078 | B1 | 151-6 |  | BOH CORRIDOR B2 EAST | REED SWITCHES | FAIL | No tamper switch installed (see photo)
TSW1079 | B2 | 651-4 |  | MDB-B B2 EAST | REED SWITCHES | FAIL | tamper not installed
TSW1080 | B2 | 651-4 |  | MDB-B B2 EAST | REED SWITCHES | FAIL | tamper not installed
TSW1081 | L1 | 710-03 | PSU1300 | FDR L1 EAST | REED SWITCHES | PASS
TSW1082 | GF | 709-03 | PSU1301 | COMMS CPB GF WEST | REED SWITCHES | PASS |  | 100% complete on ELM
TSW1083 & TSW1084 | B1 | 709-02 | PSU1302 | COMMS CPB B1 EAST | REED SWITCHES | PASS
TSW1085 | B1 | 704-01 | PSU1303 | CER B1 WEST | REED SWITCHES | PASS
TSW1086 | B1 | 704-01 | PSU1303 | CER B1 WEST | REED SWITCHES | PASS
TSW1087 | B2 | 651-02 | PSU1304 |  | REED SWITCHES | PASS
TSW1088 | B1 | 704-01 | SCADA-02 | CER B1 WEST | REED SWITCHES | FAIL | cannot test Rack Door Lock Tagged out by MTM ELECTROL SCADA TECHS
TSW1088 | B2 | 651-03 | PSU1305 | MDB-B B2 WEST | REED SWITCHES | FAIL | NOT REGISTERING ON FF
TSW1093 & TSW1094 | GF | 246-01 |  | GF - Loading bay - West | REED SWITCHES | FAIL | Unable to accesss due to height of pannels > 5m above the floor level
RTE1183 | L1 |  |  |  | DETECTION & EGRESS | N/A |  | R
CRD1173 | B1 | 151-10 |  |  |  | FAIL | CRD not installed

## Delivery circuit tests
Design Pack No. | CONTROLLER Device Name | Floor | Room No. | Room Description | Container | Device Name | Device wired as per IFC drawing | Normal / Sealed Multimeter Measurement - 5, 10, 20 K OHMs? | Abnormal / Unsealed Multimeter Measurement - 5, 10, 20 K OHMs? | Inspected by (Initials) | Date Checked | Retest 16/02/24 - Christian Heap
RSA-SDU-LOC-0924 | DGP1019 | B2 | S-03 | ESC STAIR 03 |  | RSW1233 | Yes | 10 | 20 | GC/SK | 2023-09-05 | PASS
RSA-SDU-LOC-0924 | DGP1019 | B2 | S-03 | ESC STAIR 03 |  | RSW1234 | Yes | 10 | 20 | GC/SK | 2023-09-05 | PASS
RSA-SDU-LOC-0924 | DGP1019 | B2 | S-03 | ESC STAIR 03 |  | RSW1235 | Yes | 10 | 20 | GC/SK | 2023-09-05 | PASS
RSA-SDU-LOC-0924 | DGP1014 | B1 | 151-10 | BOH CORRIDOR 10 |  | RSW1107 | Yes | 10 | 20 | SK | 2023-10-05 | PASS | AEN_DOR_B1_ESC_STAIRS_03_2
RSA-SDU-LOC-0924 | DGP1014 | B1 | 151-10 | BOH CORRIDOR 10 |  | RSW1108 | Yes | 10 | 20 | SK | 2023-10-05 | Door missing magnet - presume door has been changed
RSA-SDU-LOC-0924 | DGP1013 | B1 | S-03 | ESC STAIR 03 |  | RSW1144 | Yes | 10 | 20 | GC/SK | 2023-08-30 | PASS
RSA-SDU-LOC-0924 | DGP1013 | B1 | S-03 | ESC STAIR 03 |  | RSW1145 | Yes | 10 | 20 | GC/SK | 2023-08-30 | PASS
[6 empty] | CRD1083 | [5 empty] | 20/02/24 - crd reader faulty, will raise with CYP
[6 empty] | CRD1182(1174?) | [5 empty] | 20/02/24 - crd is for a door being sorted with RNA design and Carrier - then config to be loadedm once resolved

## Sheet1
1 | AEN_DOR_B1_ESC_STAIR_04_1 | East Emergency Stairs - Concourse | CRD 1083 Faulty. CYP defect. Christian will raise the issue with CYP.
2 | AEN_DOR_B2_ESC_STAIRS_04_1 | East Emergency Stairs - Platform | CRD 1106 Card reader has fault (Blinking Red LED). Card reader require reconfiguration according to Scott. Christian to check
3 | AEN_DOR_B2_ESC_STAIRS_03_2 | West Emergency Stairs - Platform | Wall cladding is missing and Swipe card reader CRD 1123 is not installed - will be required to test Unauthorized alarm. CYP defect
4 | AEN_DOR_B2_ESC_STAIRS_04_4 | East Emergency Stairs - Platform | Scott is not able to access Card Reader CRD1108. Christian to contact Scott
5 | AEN_DOR_B2_ESC_STAIRS_04_3 | East Emergency Stairs - Platform | Scott is not able to access Card Reader CRD1109. Christian to contact Scott
6 | AEN_DOR_B1_ESC_STAIRS_03_2 | West Emergency Stairs - Concourse | Lock (ELL1090) marked as Failed in OCS completions list. CYP defect?
7 | AEN_DOR_B1_151-3_1 | West BOH Corridor Entry - Concourse | REED switch magnet is missing. CYP defect
8 | AEN_ROL_GF_102-1_2 | Main Entrance Roller Door - Ground Floor | New Scope. Design to be finalised & added in CMS.
AEN_DOR_B1_ESC_STAIRS_03_2