## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.06.24 04:38:36.884 | DMA_TEP_0303_04_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.06.24 04:38:01.921 | DMA_TEP_0301_02_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.06.23 20:11:46.426 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.23 20:09:40.429 | SKP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.23 20:07:53.421 | SKP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.23 16:17:39.429 | SYP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.23 16:17:13.422 | SYP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.06.23 14:30:35.789 | AEN-E-PED-002 | Arden Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.06.23 13:22:28.284 | AEN_ROL_RNERV_W | West Tunnel RNERV Roller Door | RNERV crane arm extended over tracks! |  |  |  | 0 | SDU
CAME UNACK High | 2024.06.23 05:01:19.980 | PKV-E-PED-001 | Parkville Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.06.22 08:08:48.055 | PDM-Z-8301 | ZONE 8301: B1M, EPZ-A-01 | Smoke or heat detected - fire unconfirmed! |  |  |  | 0 | SDU
CAME UNACK High | 2024.06.20 08:25:18.732 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.17 17:25:05.719 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.17 17:24:47.727 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:44:45.111 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.17 09:44:45.077 | PKV_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.06.17 09:43:13.465 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:13.004 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:12.542 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:10.739 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:10.666 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:10.602 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:10.536 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:09.187 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.06.17 09:43:08.593 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK Med | 2024.06.23 14:49:30.617 | TSC-S-STN | Town Hall Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.21 08:54:21.784 | AEN-W-PSD-023 | Arden Platform 1 Zone 3 PSD 23 | Door control unit fault |  |  |  | 0 | ARN
CAME UNACK Med | 2024.06.17 17:25:05.719 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.17 10:47:01.743 | EPZ-FIP-0001 | Eastern Portal Main Fire Panel | No modbus server/gateway connection |  |  |  | 0 | SDU
CAME UNACK Med | 2024.06.17 10:46:32.867 | TSC-FIP-0001 | Town Hall Station FDCIE Panel | No modbus server/gateway connection |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.17 10:46:02.656 | TNC-FIP-0001 | State Library Station FDCIE Panel | No modbus server/gateway connection |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.17 10:35:18.075 | WPZ-FIP-0001 | Western Portal Main Fire Panel | No modbus server/gateway connection |  |  |  | 0 | SDU
CAME UNACK Med | 2024.06.17 10:35:16.887 | AEN-FIP-0001 | Arden Main Fire Panel | No modbus server/gateway connection |  |  |  | 0 | ARN
CAME UNACK Med | 2024.06.17 09:44:32.344 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.17 09:44:32.333 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.17 09:44:32.298 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.06.17 09:44:25.710 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.17 09:44:14.359 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.17 09:44:14.316 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.17 09:44:11.700 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.17 09:44:11.682 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.06.03 10:50:15.741 | _Driver1_2 | Anzac Server 2 | PSS2 S7 Driver 1 overloaded (TVCS PLC) |  |  |  | 0 | ARN
CAME UNACK Med | 2024.06.03 10:49:53.704 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:53.699 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:53.694 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:52.198 | _Mod_Plc_4_2 | MTTHL:_Mod_Plc_4_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS |  |  |  | 0 | AZC
CAME UNACK Med | 2024.06.03 10:49:52.195 | _Mod_Plc_3_2 | MTTHL:_Mod_Plc_3_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS |  |  |  | 0 | AZC
CAME UNACK Med | 2024.06.03 10:49:52.192 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.06.03 10:49:38.107 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Communications Fault - State Library Server 2 to State Library TVCS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:38.099 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Communications Fault - State Library Server 1 to State Library TVCS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.241 | _TNC-FDS-S7PLUS_2 | MTSTL:_TNC-FDS-S7PLUS_2. | Communications Fault - State Library Server 2 to State Library FDS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.239 | _TNC-FDS-S7PLUS | MTSTL:_TNC-FDS-S7PLUS. | Communications Fault - State Library Server 1 to State Library FDS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.238 | _TNC-BMS-PLC3_2 | MTSTL:_TNC-BMS-PLC3_2. | Communications Fault - State Library Server 2 to State Library BMS Gateway PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.236 | _TNC-BMS-PLC3 | MTSTL:_TNC-BMS-PLC3. | Communications Fault - State Library Server 1 to State Library BMS Gateway PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:36.234 | _TNC-BMS-PLC_2 | MTSTL:_TNC-BMS-PLC_2. | Communications Fault - State Library Server 2 to State Library BMS PLC |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:36.232 | _TNC-BMS-PLC | MTSTL:_TNC-BMS-PLC. | Communications Fault - State Library Server 1 to State Library BMS PLC |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.970 | _Mod_Plc_4_2 | MTSTL:_Mod_Plc_4_2. | Communications Fault - State Library Server 2 to State Library EWIS |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.968 | _Mod_Plc_4 | MTSTL:_Mod_Plc_4. | Communications Fault - State Library Server 1 to State Library EWIS |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.967 | _Mod_Plc_3_2 | MTSTL:_Mod_Plc_3_2. | Communications Fault - State Library Server 2 to State Library EWIS |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.964 | _Mod_Plc_3 | MTSTL:_Mod_Plc_3. | Communications Fault - State Library Server 1 to State Library EWIS |  |  |  | 0 | STL
CAME UNACK Med | 2024.06.03 10:49:34.962 | _Mod_Plc_2_2 | MTSTL:_Mod_Plc_2_2. | Communications Fault - State Library Server 2 to State Library FDS Gateway |  |  |  | 0 | THL
CAME UNACK Med | 2024.06.03 10:49:34.960 | _Mod_Plc_2 | MTSTL:_Mod_Plc_2. | Communications Fault - State Library Server 1 to State Library FDS Gateway |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.23 15:25:20.028 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | PKV | Fire Panel Fault
CAME UNACK Low | 2024.06.23 15:02:05.525 | AEN_DOR_B1_151-3_1 | Concourse west - back of house corridor | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.06.23 05:04:50.830 | PKV_DOR_B4_PKV-S-02_2 | Security Door (B4 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.23 04:34:51.460 | AEN_DOR_B2_ESC_STAIRS_04_2 | Platform 2 east - single emergency door | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.06.22 11:49:07.851 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.22 08:04:55.845 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.22 08:04:55.845 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.22 07:30:11.785 | AEN-W-PSD-030 | Arden Platform 1 Zone 3 PSD 30 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.06.22 06:49:34.735 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.22 03:28:46.168 | TNC-E-PSD-027 | State Library Platform 2 Zone 3 PSD 27 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.06.21 18:03:55.391 | PKV_DOR_B2_405-5_1 | Security Door (B2 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.21 17:29:09.064 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:29:09.064 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:27:00.159 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:27:00.159 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:26:22.109 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:26:21.063 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:25:05.062 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:25:05.062 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:24:33.064 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:24:33.064 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:22:14.126 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:20:38.105 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:20:38.105 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:19:50.168 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:17:32.122 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:17:32.122 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:13:32.105 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 17:13:32.105 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 14:33:30.846 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 14:15:40.851 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 13:55:21.870 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 13:53:48.847 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 13:53:48.847 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 13:15:21.922 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 13:11:52.916 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 12:34:18.847 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 12:34:18.847 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.21 11:03:07.023 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.21 08:58:35.788 | AEN-W-PSD-023 | Arden Platform 1 Zone 3 PSD 23 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.06.21 07:15:19.115 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.21 07:14:26.232 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.21 07:13:14.243 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.20 14:08:34.764 | PKV_DOR_B4_PKV-S-01_1 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.20 11:40:56.861 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.20 08:56:21.143 | DMA-FIP-0001 | Anzac Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | AZC | Fire Panel Fault
CAME UNACK Low | 2024.06.19 19:57:41.853 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.19 19:57:36.840 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.19 19:57:05.868 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.19 19:57:00.848 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.19 11:10:16.913 | PKV_DOR_B2_PKV-S-02_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.18 17:20:18.162 | TNC-E-PSD-016 | State Library Platform 2 Zone 2 PSD 16 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.06.17 15:36:14.088 | EPZ-FIP-0001 | Eastern Portal Main Fire Panel | Fire panels in the station have a fault |  |  |  | 0 | SDU | Fire Panel Fault
CAME UNACK Low | 2024.06.17 10:17:22.155 | _ReduManager | Distributed Server 1 | Server 1 - Set active automatically |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 10:14:18.577 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.06.17 09:48:38.267 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:38.246 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:38.209 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:38.177 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:38.154 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:38.131 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.06.17 09:48:31.349 | PKV_DOR_B2_PKV-S-03_3 | Security Door (B2 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.06.17 09:47:22.030 | AEN-SPE-0403 | B1, AEN-SPE-0403, 103-2 PAID CONC | Heat or smoke detector fault |  |  |  | 0 | ARN | Fire System Currently under Test
CAME UNACK Low | 2024.06.17 09:47:21.408 | AEN-SPE-0400 | B1, AEN-SPE-0400, 103-2 PAID CONC | Heat or smoke detector fault |  |  |  | 0 | ARN | Fire System Currently under Test
CAME UNACK Low | 2024.06.17 09:46:39.288 | AEN-SPE-0095 | B1, AEN-SPE-0095, 103-2 PAID CONC | Heat or smoke detector fault |  |  |  | 0 | ARN | Fire System Currently under Test
CAME UNACK Low | 2024.06.17 09:46:38.386 | AEN-SPE-0090 | B1, AEN-SPE-0090, 151-10 BOH Corridor | Heat or smoke detector fault |  |  |  | 0 | ARN | Fire System Currently under Test
CAME UNACK Low | 2024.06.17 09:44:06.674 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.17 09:43:58.781 | AEN_TEXA | Tunnel Ambient Temperature Control - Eastbound | Temperature Sensors A - Discrepancy |  |  |  | 0 | SDU | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.06.17 09:43:48.039 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | Door status indicator fault |  |  |  | 0 | PKV
CAME UNACK Low | 2024.06.17 09:43:47.837 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.06.17 09:43:25.896 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.06.03 10:49:38.104 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Link Failure - State Library Server 2 to State Library TVCS CPU 2 |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.03 10:49:38.101 | _TNC-TVC-PLC_2 | MTSTL:_TNC-TVC-PLC_2. | Link Failure - State Library Server 2 to State Library TVCS CPU 1 |  |  |  | 0 | THL
CAME UNACK Low | 2024.06.03 10:49:38.095 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Link Failure - State Library Server 1 to State Library TVCS CPU 2 |  |  |  | 0 | STL
CAME UNACK Low | 2024.06.03 10:49:38.091 | _TNC-TVC-PLC | MTSTL:_TNC-TVC-PLC. | Link Failure - State Library Server 1 to State Library TVCS CPU 1 |  |  |  | 0 | STL
WENT UNACK Med | 2024.06.21 11:01:00.074 | _PKV-BMS-PLC_2 | MTPKV:_PKV-BMS-PLC_2. | Communications Fault - Parkville Server 2 to Parkville BMS PLC |  |  | 2024.06.21 11:01:03.648 | 0 | STL
WENT UNACK Med | 2024.06.21 11:00:35.092 | _PKV-BMS-PLC | MTPKV:_PKV-BMS-PLC. | Communications Fault - Parkville Server 1 to Parkville BMS PLC |  |  | 2024.06.21 11:00:38.540 | 0 | PKV
WENT UNACK Med | 2024.06.21 10:13:15.006 | _Mod_Plc_2_2 | MTPKV:_Mod_Plc_2_2. | Communications Fault - Parkville Server 2 to Parkville FDS Gateway |  |  | 2024.06.21 10:14:23.028 | 0 | STL
WENT UNACK Med | 2024.06.21 10:13:14.995 | _Mod_Plc_2 | MTPKV:_Mod_Plc_2. | Communications Fault - Parkville Server 1 to Parkville FDS Gateway |  |  | 2024.06.21 10:14:23.002 | 0 | STL
ACK High | 2024.06.23 04:46:43.786 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.06.23 10:02:11.994 | sergio_paniagua |  | 0 | ARN | PED Opening
ACK High | 2024.06.23 04:43:17.787 | AEN-E-PED-001 | Arden Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.06.23 09:18:02.789 | sergio_paniagua |  | 0 | ARN | PED Opening
ACK High | 2024.05.20 08:23:30.503 | _Driver2 | MTTHL:_Driver2. | Driver overloaded | 2024.05.20 15:17:54.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.10 08:49:20.968 | _Driver2_2 | MTTHL:_Driver2_2. | Driver overloaded | 2024.05.20 15:17:59.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.06.21 12:28:48.176 | TNC-S-STN | State Library Station PSD System | PSD lost connection to signalling system! | 2024.06.24 07:23:43.058 | kai_longley |  | 0 | STL
ACK Med | 2024.06.17 10:47:01.691 | DMA-FIP-0001 | Anzac Station FDCIE Panel | No modbus server/gateway connection | 2024.06.17 14:28:57.072 | emilio_ito |  | 0 | AZC
ACK Med | 2024.06.17 10:43:09.320 | PKV-FIP-0001 | Parkville Station FDCIE Panel | No modbus server/gateway connection | 2024.06.21 07:00:25.850 | emilio_ito |  | 0 | PKV
ACK Med | 2024.06.03 10:48:16.689 | _Driver1_2 | MTARD:_Driver1_2. | PSS2 S7 Driver 1 overloaded (TVCS PLC) | 2024.06.04 08:54:10.389 | sergio_paniagua |  | 0 | PKV
ACK Med | 2024.06.03 10:47:25.340 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.339 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.338 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.336 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.335 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.334 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.333 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.332 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.06.03 10:47:25.306 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.06.03 10:47:25.291 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.06.21 16:19:21.058 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault | 2024.06.21 16:25:52.047 | josh_estrada |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.06.20 13:54:38.119 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.06.20 14:57:08.354 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.06.20 13:50:49.685 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Unauthorised access | 2024.06.20 14:57:10.363 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.06.20 13:01:36.118 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.06.20 14:57:12.884 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.06.19 13:03:52.119 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault | 2024.06.20 14:57:17.162 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.06.19 13:02:35.024 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault | 2024.06.20 14:57:19.656 | harsimran_virk |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.06.17 09:48:30.818 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.06.20 14:57:28.000 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.06.17 09:47:22.356 | AEN-SPE-0404 | B1, AEN-SPE-0404, 151-10 BOH Corridor | Heat or smoke detector fault | 2024.06.20 14:57:33.157 | harsimran_virk |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.06.03 10:47:25.310 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.06.03 10:47:25.308 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.06.03 10:47:25.302 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.06.03 10:47:25.299 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.06.03 12:19:48.554 | eric_maddocks |  | 0 | ARN | Servers Comms