## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.05.08 00:01:04.122 | DMA_TEP_0303_04_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.05.08 00:01:03.366 | PKV_TEP_0301_02_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | PKV
CAME UNACK High | 2024.05.08 00:01:03.366 | PKV_TEP_0303_04_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | PKV
CAME UNACK High | 2024.05.07 20:55:46.316 | PKV-W-PED-001 | Parkville Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.07 20:55:32.309 | PKV-E-PED-002 | Parkville Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.07 19:19:16.312 | TNC-W-PED-001 | State Library Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.07 19:13:18.333 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.07 19:01:04.576 | TSC-W-PED-001 | Town Hall Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.07 14:33:24.957 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.07 14:15:35.973 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.07 14:13:49.974 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.06 13:49:44.822 | SYP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 13:21:29.819 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 09:24:49.474 | TSC-W-PSD-030 | Town Hall Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.06 09:24:37.553 | TSC-W-PSD-010 | Town Hall Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.06 09:24:19.513 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD obstructed on opening or closing! |  |  |  | 0 | THL | PSD obstructed
CAME UNACK High | 2024.05.06 09:12:45.472 | SKP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.06 09:09:04.993 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.06 09:09:04.983 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.06 09:07:20.816 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.901 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.893 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.885 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.877 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.740 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:17.148 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:16.563 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.06 09:07:15.973 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK Med | 2024.05.07 14:15:35.973 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 10:11:47.716 | _Mod_Plc_4_2 | MTPKV:_Mod_Plc_4_2. | ommunications Fault - Parkville Server 2 to Parkville EWIS |  |  |  | 0 | STL | Servers Comms
CAME UNACK Med | 2024.05.06 10:01:43.984 | _Mod_Plc_1 | Anzac Server 1 | Communications Fault - Anzac Server 1 to Anzac PSD |  |  |  | 0 | AZC | Servers Comms
CAME UNACK Med | 2024.05.06 09:25:01.163 | TSC-S-STN | Town Hall Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | THL | Servers Comms
CAME UNACK Med | 2024.05.06 09:10:37.753 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Emergency Intercom Activated Level 2 |  |  |  | 0 | AZC
CAME UNACK Med | 2024.05.06 09:08:30.972 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:30.969 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:20.849 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:17.878 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.06 09:08:17.874 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Low | 2024.05.08 05:20:09.728 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.727 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.726 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.726 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.726 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 05:20:09.724 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.08 00:12:06.087 | AEN-FIP-0001 | Arden Main Fire Panel | Fire panels in the station have a fault |  |  |  | 0 | ARN | Fire Panel Fault
CAME UNACK Low | 2024.05.07 20:39:10.093 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 16:50:30.202 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 16:15:32.008 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.07 15:26:50.862 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 15:09:17.010 | DMA_ESC_0004 | Escalator 4 Bank 3 (B2 Basement to B1 Basement) | Escalator stopped.(emergency brake fault) |  |  |  | 0 | AZC
CAME UNACK Low | 2024.05.07 14:40:32.358 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 14:40:32.358 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 14:03:16.023 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 12:45:51.387 | PKV_FCU_1207_MCV_02 | Fan Coil Unit - Hot Water Valve | Modulated device position discrepancy fault alarm |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.07 12:45:46.279 | PKV_FCU_1207_MCV_01 | Fan Coil Unit - Chilled Water Valve | Modulated device position discrepancy fault alarm |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.07 10:37:18.224 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 10:37:18.224 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 10:37:18.214 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 10:37:18.214 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 10:37:18.214 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 09:16:13.328 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.07 07:50:30.785 | PKV_DOR_B4_PKV-S-02_1 | Security Door (B4 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.07 07:38:36.645 | PKV_DOR_B4_PKV-S-01_2 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 16:27:06.174 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 16:26:56.202 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 10:38:29.085 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Low | 2024.05.06 10:38:29.076 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 |  |  |  | 0 | THL | Servers Comms
CAME UNACK Low | 2024.05.06 10:38:23.547 | _Mod_Plc_1_2 | Distributed Server 1 | Communications Fault - Distributed Server 2 to RSG |  |  |  | 0 | THL | Servers Comms
CAME UNACK Low | 2024.05.06 09:24:19.432 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:24:18.770 | TSC-E-PSD-009 | Town Hall Platform 2 Zone 1 PSD 09 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:13:17.271 | DMA-SPE-0928 | B1, DMA-SPE-0928 OP MALE STAFF LCK 221-1 | Heat or smoke detector fault |  |  |  | 0 | AZC | Fire System Currently under Test
CAME UNACK Low | 2024.05.06 09:12:44.076 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:44.048 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:44.004 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.963 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.937 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:43.908 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.06 09:12:37.783 | PKV_DOR_B4_PKV-S-01_3 | Security Door (B4 WEST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 09:12:37.638 | PKV_DOR_B2_406-14_2 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 09:12:37.580 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.06 09:10:41.883 | PKV_LFT_0010 | Lift 10 BOH (B4 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:41.775 | PKV_LFT_0010 | Lift 10 BOH (B4 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:41.310 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:40.910 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:40.801 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:40.293 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:39.894 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:39.785 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:38.878 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:38.769 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:37.931 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:37.862 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:37.753 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:36.205 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:35.679 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:35.561 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:34.706 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:34.588 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:34.178 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:10:34.067 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:09:02.567 | DMA_ESC_0012 | Escalator 12 Bank 7 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.06 09:09:01.758 | DMA_ESC_0011 | Escalator 11 Bank 7 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:58.871 | DMA_ESC_0007 | Escalator 7 Bank 5 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:58.066 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:55.164 | DMA_ESC_0002 | Escalator 2 Bank 2 (B2 Basement to B1 Basement) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:50.121 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:49.343 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:48.560 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:46.196 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:45.409 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:42.286 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:41.504 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:40.731 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:39.958 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:39.183 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:38.414 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.06 09:08:16.052 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.06 09:07:56.289 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.06 09:07:34.198 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | Door status indicator fault |  |  |  | 0 | STL
CAME UNACK Low | 2024.05.06 09:07:33.965 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
ACK High | 2024.05.06 09:09:56.866 | AEN-E-PED-002 | Arden Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! | 2024.05.07 11:11:31.394 | dominic_dlasselle |  | 0 | ARN | PED Opening
ACK High | 2024.05.06 09:08:17.159 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! | 2024.05.07 11:11:28.284 | dominic_dlasselle |  | 0 | ARN | PED Opening
ACK High | 2024.05.06 09:07:53.952 | AEN-W-PSD-030 | Arden Platform 1 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:25.224 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:50.397 | AEN-W-PSD-021 | Arden Platform 1 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:21.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:46.057 | AEN-W-PSD-010 | Arden Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:19.282 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:42.500 | AEN-W-PSD-001 | Arden Platform 1 Zone 1 PSD 01 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:16.395 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:42.056 | AEN-E-PSD-030 | Arden Platform 2 Zone 3 PSD 30 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:13.880 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:41.617 | AEN-E-PSD-029 | Arden Platform 2 Zone 3 PSD 29 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:11.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:41.176 | AEN-E-PSD-028 | Arden Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:08.959 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:40.736 | AEN-E-PSD-027 | Arden Platform 2 Zone 3 PSD 27 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:05.281 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:40.288 | AEN-E-PSD-026 | Arden Platform 2 Zone 3 PSD 26 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:02.688 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:39.848 | AEN-E-PSD-025 | Arden Platform 2 Zone 3 PSD 25 | PSD Unscheduled Door Opening! | 2024.05.07 11:11:00.161 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:39.406 | AEN-E-PSD-024 | Arden Platform 2 Zone 3 PSD 24 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:56.360 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.966 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:53.690 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.524 | AEN-E-PSD-022 | Arden Platform 2 Zone 3 PSD 22 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:50.622 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:38.081 | AEN-E-PSD-021 | Arden Platform 2 Zone 2 PSD 21 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:46.885 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:37.633 | AEN-E-PSD-020 | Arden Platform 2 Zone 2 PSD 20 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:36.688 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:37.189 | AEN-E-PSD-019 | Arden Platform 2 Zone 2 PSD 19 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:05.878 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:36.748 | AEN-E-PSD-018 | Arden Platform 2 Zone 2 PSD 18 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:33.624 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:36.298 | AEN-E-PSD-017 | Arden Platform 2 Zone 2 PSD 17 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:28.595 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:35.859 | AEN-E-PSD-016 | Arden Platform 2 Zone 2 PSD 16 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:26.276 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:35.420 | AEN-E-PSD-015 | Arden Platform 2 Zone 2 PSD 15 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:23.623 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.980 | AEN-E-PSD-014 | Arden Platform 2 Zone 2 PSD 14 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:18.900 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.541 | AEN-E-PSD-013 | Arden Platform 2 Zone 2 PSD 13 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:21.491 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:34.099 | AEN-E-PSD-012 | Arden Platform 2 Zone 2 PSD 12 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:16.136 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:33.658 | AEN-E-PSD-011 | Arden Platform 2 Zone 2 PSD 11 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:12.867 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK High | 2024.05.06 09:07:33.212 | AEN-E-PSD-010 | Arden Platform 2 Zone 2 PSD 10 | PSD Unscheduled Door Opening! | 2024.05.07 11:10:10.162 | dominic_dlasselle |  | 0 | ARN | PSD Opening
ACK Med | 2024.05.06 11:54:12.166 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.05.06 12:03:26.229 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.06 11:54:12.159 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Med | 2024.05.06 10:38:29.113 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.110 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.108 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.106 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.104 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.102 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.101 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:38:29.099 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.06 11:54:59.156 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.06 10:13:53.480 | _Mod_Plc_1_2 | Anzac Server 2 | Communications Fault - Anzac Server 2 to Anzac PSD | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Med | 2024.05.06 09:08:34.594 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2024.05.06 09:08:34.583 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2024.05.06 09:08:34.544 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault | 2024.05.07 11:17:43.586 | liam_walkerchan |  | 0 | ARN | Comms fault to be investigated
ACK Med | 2023.10.10 08:29:53.877 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Med | 2023.10.10 08:29:53.243 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Med | 2023.10.10 08:29:52.927 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | THL | Servers Comms
ACK Med | 2023.10.10 08:29:49.030 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway | 2023.11.28 08:35:41.398 | chris_lawson |  | 0 | AZC | Servers Comms
ACK Low | 2024.05.06 11:54:12.186 | _ReduManager | Distributed Server 1 | Server 1 - Set active automatically | 2024.05.06 12:03:12.642 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 10:38:29.082 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 10:38:29.074 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.07 11:17:43.625 | liam_walkerchan |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.06 09:12:37.455 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:12:37.337 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Unauthorised access | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:12:37.328 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Door open too long | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:12:37.312 | AEN_DOR_B2_ESC_STAIRS_04_2 | Platform 2 east - single emergency door | Unauthorised access | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:12:37.196 | AEN_DOR_B1_151-4_1 | Concourse east - back of house emergency corridor | Unauthorised access | 2024.05.07 11:07:42.106 | dominic_dlasselle |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.06 09:10:16.956 | AEN-FLS-0008 | GF, AEN-FLS-0008, SCV1-RETAIL 1 Spr.F/S | Heat or smoke detector fault | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.05.06 09:09:52.680 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.06 09:09:52.279 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.06 09:09:51.473 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | General fault alarm as a result of loss of power
ACK Low | 2024.05.06 09:08:39.397 | AEN_ESC_0007 | Escalator 7 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.06 09:08:38.731 | AEN_ESC_0006 | Escalator 6 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.06 09:08:38.066 | AEN_ESC_0005 | Escalator 5 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.07 11:07:42.004 | dominic_dlasselle |  | 0 | ARN | Escalators out of service