## Sheet1
Severity | Alarm Raised | Asset ID | Asset Name | Alarm Description | Acknowledged | By | Cleared | Comments | Location | Test Comment
CAME UNACK High | 2024.05.28 03:28:51.038 | DMA_TEP_0303_04_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.05.28 03:28:27.041 | DMA_TEP_0301_02_DS | Tunnel Drainage Pump - Duty Selection | Risk of track flooding! |  |  |  | 0 | AZC
CAME UNACK High | 2024.05.27 17:04:27.660 | AEN-W-PED-002 | Arden Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.05.27 15:38:22.124 | TSC-E-PED-002 | Town Hall Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.27 15:36:07.604 | PKV_OFN_0001_03_DS | Over Track Exhaust Fan 01 - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.27 15:33:56.122 | TSC-W-PED-001 | Town Hall Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | THL | PED Opening
CAME UNACK High | 2024.05.27 15:08:05.605 | PKV_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.27 15:08:05.605 | PKV_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.27 14:12:46.468 | TSC-E-PSD-029 | Town Hall Platform 2 Zone 3 PSD 29 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.27 14:12:46.439 | TSC-W-PSD-023 | Town Hall Platform 1 Zone 3 PSD 23 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.27 14:12:46.363 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | THL | PSD Opening
CAME UNACK High | 2024.05.27 12:30:45.663 | AEN-E-PED-001 | Arden Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.05.27 11:20:56.116 | TNC-E-PED-001 | State Library Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.27 10:47:26.125 | TNC-E-PED-002 | State Library Platform 2 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.27 07:34:31.687 | AEN_OFN_0101_02_DS | Over Track Exhaust Fan - West End - Duty Selection | Arden - West End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.25 22:03:44.140 | TNC-W-EED-040 | State Library Platform 1 Zone 3 EED 40 | EED Unscheduled Door Opening! |  |  |  | 0 | STL
CAME UNACK High | 2024.05.25 14:44:39.658 | AEN-W-PED-001 | Arden Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | ARN | PED Opening
CAME UNACK High | 2024.05.24 21:27:41.591 | DMA_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.24 21:27:02.550 | DMA_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.24 21:26:57.561 | DMA_OFN_0101_02_DS | Over Track Exhaust Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.24 21:26:53.552 | DMA_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | AZC | TVCS Fans out of service
CAME UNACK High | 2024.05.24 20:35:07.559 | DMA_SSX_0002 | TVCS Shaft Smoke Detection System 02 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.24 17:21:31.602 | PKV_TFN_0201_03_DS | Tunnel Ventilation Fan 01 - East End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.24 17:18:31.682 | AEN_TFN_0201_03_DS | Tunnel Ventilation Fan - East End - Duty Selection | Tunnel Section 03 Arden End - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.24 17:18:28.701 | AEN_OFN_0201_02_DS | Over Track Exhaust Fan - East End - Duty Selection | Arden - East End Over Track Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.24 17:18:23.609 | PKV_TFN_0101_03_DS | Tunnel Ventilation Fan 01 - West End - Duty Selection | All fans inoperative! |  |  |  | 0 | PKV | TVCS Fans out of service
CAME UNACK High | 2024.05.24 17:18:03.689 | AEN_TFN_0101_03_DS | Tunnel Ventilation Fan - West End - Duty Selection | Tunnel Section 01 - Ventilation Unavailable! |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK High | 2024.05.24 11:46:40.119 | TNC-W-PED-002 | State Library Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.24 07:34:28.117 | TNC-W-PED-001 | State Library Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | STL | PED Opening
CAME UNACK High | 2024.05.23 18:01:49.773 | PKV-W-PED-002 | Parkville Platform 1 PED 02 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.23 17:13:37.546 | DMA_SSX_0001 | TVCS Shaft Smoke Detection System 01 | Shaft smoke detection unavailable! |  |  |  | 0 | SDU | Smoke sensors not commisioned yet
CAME UNACK High | 2024.05.23 12:46:19.773 | PKV-E-PED-001 | Parkville Platform 2 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.23 12:08:19.969 | PKV-E-PSD-021 | Parkville Platform 2 Zone 2 PSD 21 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.968 | PKV-E-PSD-019 | Parkville Platform 2 Zone 2 PSD 19 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.968 | PKV-E-PSD-020 | Parkville Platform 2 Zone 2 PSD 20 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.965 | PKV-E-PSD-018 | Parkville Platform 2 Zone 2 PSD 18 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-005 | Parkville Platform 2 Zone 1 PSD 05 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-006 | Parkville Platform 2 Zone 1 PSD 06 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-007 | Parkville Platform 2 Zone 1 PSD 07 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-008 | Parkville Platform 2 Zone 1 PSD 08 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-009 | Parkville Platform 2 Zone 1 PSD 09 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-010 | Parkville Platform 2 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-011 | Parkville Platform 2 Zone 2 PSD 11 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-012 | Parkville Platform 2 Zone 2 PSD 12 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-013 | Parkville Platform 2 Zone 2 PSD 13 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-014 | Parkville Platform 2 Zone 2 PSD 14 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-015 | Parkville Platform 2 Zone 2 PSD 15 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-016 | Parkville Platform 2 Zone 2 PSD 16 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.778 | PKV-E-PSD-017 | Parkville Platform 2 Zone 2 PSD 17 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.777 | PKV-E-PSD-001 | Parkville Platform 2 Zone 1 PSD 01 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.777 | PKV-E-PSD-002 | Parkville Platform 2 Zone 1 PSD 02 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.777 | PKV-E-PSD-003 | Parkville Platform 2 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 12:08:19.777 | PKV-E-PSD-004 | Parkville Platform 2 Zone 1 PSD 04 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.23 04:31:19.801 | SYP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.22 18:25:45.969 | PKV-W-PSD-021 | Parkville Platform 1 Zone 2 PSD 21 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.968 | PKV-W-PSD-019 | Parkville Platform 1 Zone 2 PSD 19 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.953 | PKV-W-PSD-018 | Parkville Platform 1 Zone 2 PSD 18 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.865 | PKV-W-PSD-016 | Parkville Platform 1 Zone 2 PSD 16 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.865 | PKV-W-PSD-017 | Parkville Platform 1 Zone 2 PSD 17 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.833 | PKV-W-PSD-015 | Parkville Platform 1 Zone 2 PSD 15 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.823 | PKV-W-PSD-012 | Parkville Platform 1 Zone 2 PSD 12 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.823 | PKV-W-PSD-013 | Parkville Platform 1 Zone 2 PSD 13 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-004 | Parkville Platform 1 Zone 1 PSD 04 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-005 | Parkville Platform 1 Zone 1 PSD 05 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-006 | Parkville Platform 1 Zone 1 PSD 06 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-007 | Parkville Platform 1 Zone 1 PSD 07 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-008 | Parkville Platform 1 Zone 1 PSD 08 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-009 | Parkville Platform 1 Zone 1 PSD 09 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.790 | PKV-W-PSD-010 | Parkville Platform 1 Zone 2 PSD 10 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.789 | PKV-W-PSD-001 | Parkville Platform 1 Zone 1 PSD 01 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:25:45.789 | PKV-W-PSD-003 | Parkville Platform 1 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:15:37.765 | PKV-W-PED-001 | Parkville Platform 1 PED 01 | Platform End Door Unscheduled Door Opening! |  |  |  | 0 | PKV | PED Opening
CAME UNACK High | 2024.05.22 18:11:37.792 | PKV-W-PSD-020 | Parkville Platform 1 Zone 2 PSD 20 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 18:11:37.774 | PKV-W-PSD-002 | Parkville Platform 1 Zone 1 PSD 02 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 16:39:37.789 | PKV-W-PSD-029 | Parkville Platform 1 Zone 3 PSD 29 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 16:39:37.772 | PKV-W-PSD-011 | Parkville Platform 1 Zone 2 PSD 11 | PSD Unscheduled Door Opening! |  |  |  | 0 | PKV | PSD Opening
CAME UNACK High | 2024.05.22 04:23:26.807 | SYP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.22 04:23:15.810 | SYP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.21 14:29:20.808 | SYP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.441 | SKP-ZONE-0004 | Westbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.382 | SKP-ZONE-0003 | Westbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.316 | SKP-ZONE-0002 | Eastbound Detection Zone 2 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:41:01.264 | SKP-ZONE-0001 | Eastbound Detection Zone 1 | TIAS activated! |  |  |  | 0 | SDU | TIAS
CAME UNACK High | 2024.05.20 11:36:37.323 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK High | 2024.05.20 11:36:32.084 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD Unscheduled Door Opening! |  |  |  | 0 | AZC | PSD Opening
CAME UNACK Med | 2024.05.28 07:37:16.714 | PKV_FCU_0211_FG | Fan Coil Unit - Function Group | Cooling unavailable! |  |  |  | 0 | PKV
CAME UNACK Med | 2024.05.28 07:37:16.700 | PKV_FCU_1219_FG | Fan Coil Unit - Function Group | Cooling unavailable! |  |  |  | 0 | PKV
CAME UNACK Med | 2024.05.28 07:37:16.700 | PKV_FCU_0213_FG | Fan Coil Unit - Function Group | Cooling unavailable! |  |  |  | 0 | PKV
CAME UNACK Med | 2024.05.27 17:20:42.561 | AEN_TEP_0303_05_DS | Tunnel Drainage Pump - Duty Selection | Tunnel drainage pit - reduced capability! |  |  |  | 0 | ARN
CAME UNACK Med | 2024.05.27 15:36:07.604 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.27 14:12:46.129 | TSC-S-STN | Town Hall Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | THL
CAME UNACK Med | 2024.05.27 13:39:54.788 | _Mod_Plc_1_2 | Parkville Server 2 | Communications Fault - Parkville Server 2 to Parkville PSD Servers |  |  |  | 0 | STL
CAME UNACK Med | 2024.05.27 13:39:54.773 | _Mod_Plc_1 | Parkville Server 1 | Communications Fault - Parkville Server 1 to Parkville PSD Servers |  |  |  | 0 | PKV
CAME UNACK Med | 2024.05.27 07:34:31.687 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Station Ventilation (OTE) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.25 09:27:48.714 | AEN_ATSComm | RSG Modbus | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.05.24 21:27:02.550 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Over Track Exhaust Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.24 21:26:53.552 | DMA_ModeSts | TVCS Mode Status - Domain Station S10 | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.24 17:18:23.609 | PKV_ModeSts | TVCS Section 04 Parkville Station mode status | Tunnel section ventilation unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.24 17:18:03.689 | AEN_ModeSts | TVCS Section 02 Arden Station mode status | Tunnel Section Ventilation (TVS) Unavailable |  |  |  | 0 | SDU | TVCS Fans out of service
CAME UNACK Med | 2024.05.20 11:37:01.190 | AEN_TSCComm | CBD South TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.05.20 11:37:01.179 | AEN_TNCComm | CBS North TVCS PLC | HCS/ATS communication fault |  |  |  | 0 | ARN | Comms fault to be investigated
CAME UNACK Med | 2024.05.20 11:35:27.847 | PKV-S-STN | Parkville Station PSD System | PSD lost connection to signalling system! |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:38:01.939 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:38:01.939 | DMA_LFT_0007 | Lift 7 BOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:37:16.710 | PKV_FCU_0217_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:37:16.710 | PKV_FCU_0215_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:37:16.700 | PKV_FCU_1119_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:37:16.700 | PKV_FCU_0205_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:37:16.700 | PKV_FCU_0203_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:34:19.002 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:32:26.153 | PKV-SPE-0521 | B2, PKV-SPE-0521 BOH PLANT ENTRY 151-1 | Heat or smoke detector fault |  |  |  | 0 | PKV | Fire System Currently under Test
CAME UNACK Low | 2024.05.28 07:30:26.691 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:28:42.028 | PKV-FIP-0001 | Parkville Station FDCIE Panel | Fire panels in the station have a fault |  |  |  | 0 | PKV | Fire Panel Fault
CAME UNACK Low | 2024.05.28 07:28:28.735 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:28:26.681 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:28:26.681 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:28:22.706 | PKV_FCU_1123_FG | Fan Coil Unit - Function Group | Heating / cooling unavailable |  |  |  | 0 | PKV
CAME UNACK Low | 2024.05.28 07:17:12.168 | AEN_DOR_GF_246-1_2 | Ground floor west - loading dock 2 | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.28 07:12:17.659 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:09:14.688 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:08:20.690 | PKV_LFT_0008 | Lift 8 BOH (Platforms to B3 Basement) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:05:53.654 | PKV_LFT_0006 | Lift 6 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 07:03:38.794 | AEN_DOR_GF_405-2_1 | Ground floor east - emergency escape ramp | Door open too long |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.28 06:59:41.655 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 06:59:41.655 | PKV_LFT_0011 | Lift 11 BOH (B1 Basement to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 06:49:14.686 | PKV_LFT_0007 | Lift 7 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.28 05:31:34.671 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift monitoring lost |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:32:07.655 | PKV_ESC_0009 | Escalator 9 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:30:56.668 | PKV_ESC_0008 | Escalator 8 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:29:34.666 | PKV_ESC_0007 | Escalator 7 Bank 4 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:27:19.655 | PKV_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:27:06.678 | PKV_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:21:18.712 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:18:55.653 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:15:40.669 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:13:56.666 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:09:49.652 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:08:10.668 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 23:04:32.682 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:04:32.682 | PKV_LFT_0005 | Lift 5 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:03:03.662 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:03:02.679 | PKV_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 23:02:04.673 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift safety feature fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 22:59:42.665 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:58:54.661 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:57:37.648 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:56:47.649 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator communications lost |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.169 | PKV_ESC_0007 | Escalator 7 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0001 | Escalator 1 Bank 1 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0002 | Escalator 2 Bank 1 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0003 | Escalator 3 Bank 2 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0004 | Escalator 4 Bank 2 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0005 | Escalator 5 Bank 3 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.168 | PKV_ESC_0006 | Escalator 6 Bank 3 (Platforms to Concourse) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0009 | Escalator 9 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0010 | Escalator 10 Bank 5 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0011 | Escalator 11 Bank 5 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0012 | Escalator 12 Bank 6 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0013 | Escalator 13 Bank 6 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0015 | Escalator 15 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.022 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:53:20.021 | PKV_ESC_0008 | Escalator 8 Bank 4 (Concourse to Ground Floor) | Escalator fire response isolated |  |  |  | 0 | PKV | Escalators out of service
CAME UNACK Low | 2024.05.27 22:51:15.660 | PKV_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | PKV | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 16:35:57.664 | AEN-E-PSD-023 | Arden Platform 2 Zone 3 PSD 23 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 16:01:11.011 | DMA_LFT_0006 | Lift 6 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 15:53:35.922 | DMA_LFT_0008 | Lift 8 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 15:05:01.009 | DMA_LFT_0009 | Lift 9 BOH (B2 Basement to B1 Basement) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.27 14:12:46.146 | TSC-E-PSD-029 | Town Hall Platform 2 Zone 3 PSD 29 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 14:12:46.142 | TSC-E-PSD-016 | Town Hall Platform 2 Zone 2 PSD 16 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 14:12:46.141 | TSC-E-PSD-007 | Town Hall Platform 2 Zone 1 PSD 07 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 14:12:46.141 | TSC-E-PSD-010 | Town Hall Platform 2 Zone 2 PSD 10 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 14:12:46.135 | TSC-W-PSD-023 | Town Hall Platform 1 Zone 3 PSD 23 | PSD isolated |  |  |  | 0 | THL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 11:30:14.697 | _ReduManager | Distributed Server 1 | Server 1 - Set active automatically |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 11:28:18.014 | S_98_1_14850 | Traction Section Anzac to South Yarra | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.014 | S_99_1_14851 | Traction Section Anzac to South yarra section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_91_1_14652 | Traction Section Arden Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_91_2_14653 | Traction Section Arden to Parkville section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_92_1_14700 | Traction Section Parkville Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_93_1_14702 | Traction Section Parkville Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_94_1_14750 | Traction Section State Library Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_94_3_14752 | Traction Section Town Hall Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_95_1_14753 | Traction Section State Library Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_95_3_14755 | Traction Section Town Hall Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_96_1_14800 | Traction Section Town Hall to Anzac | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.013 | S_97_1_14802 | Traction Section Town Hall to Anzac section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.012 | S_88_1_14600 | Traction Section Footscray west to Arden | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.012 | S_89_1_14603 | Traction Section Footscray west to Arden section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.012 | S_90_1_14650 | Traction Section Arden Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.012 | S_90_2_14651 | Traction Section Arden to Parkville | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.27 11:28:18.009 | essGeneral | ESS Overall health Status | ELECTROL SCADA System Timeout. All Traction Power State Unknown. |  |  |  | 0 | SDU
CAME UNACK Low | 2024.05.27 10:09:35.857 | _ReduManager_2 | Town Hall Server 2 | Server 2 - Set active automatically |  |  |  | 0 | AZC
CAME UNACK Low | 2024.05.27 08:41:02.124 | TNC-W-PSD-025 | State Library Platform 1 Zone 3 PSD 25 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 08:31:44.122 | TNC-E-PSD-025 | State Library Platform 2 Zone 3 PSD 25 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 07:49:28.401 | DMA_ESC_0006 | Escalator 6 Bank 4 (B1 Basement to GF Gound Floor) | Escalator communications lost |  |  |  | 0 | AZC | Escalators out of service
CAME UNACK Low | 2024.05.27 07:29:37.658 | AEN-W-PSD-009 | Arden Platform 1 Zone 1 PSD 09 | PSD isolated |  |  |  | 0 | ARN | PSD isolated during a blockade
CAME UNACK Low | 2024.05.27 06:19:48.395 | DMA_LFT_0003 | Lift 3 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 18:08:00.537 | DMA_TEXA | Tunnel Ambient Temperature Control | Temperature Sensors A - Discrepancy |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:27:07.395 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:27:07.395 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift monitoring lost |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:58.398 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:58.398 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift General Fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:57.394 | DMA_LFT_0001 | Lift 1 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:57.394 | DMA_LFT_0002 | Lift 2 FOH (B2 Basement to B1 Basement) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:57.394 | DMA_LFT_0004 | Lift 4 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.26 15:26:57.394 | DMA_LFT_0005 | Lift 5 FOH (B1 Basement to GF Gound Floor) | Lift safety feature fault |  |  |  | 0 | AZC | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.24 13:46:59.084 | AEN_LFT_0001 | Lift 1 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.24 13:46:55.084 | AEN_LFT_0002 | Lift 2 FOH (Platforms to Concourse) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.24 13:46:51.093 | AEN_LFT_0003 | Lift 3 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.24 13:46:47.975 | AEN_LFT_0004 | Lift 4 FOH (Concourse to Ground Floor) | Lift General Fault |  |  |  | 0 | ARN | General fault alarm as a result of loss of power
CAME UNACK Low | 2024.05.24 12:27:03.771 | PKV_DOR_B2_151-10_1 | Security Door (B2 EAST) | Unauthorised access |  |  |  | 0 | PKV | Door forced open without using a valid card
CAME UNACK Low | 2024.05.23 10:09:27.296 | AEN_DOR_B2_ESC_STAIRS_04_2 | Platform 2 east - single emergency door | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.22 20:42:52.141 | AEN_DOR_B2_ESC_STAIRS_04_1 | Platform 2 east - single emergency door | Unauthorised access |  |  |  | 0 | ARN | Door forced open without using a valid card
CAME UNACK Low | 2024.05.20 11:40:59.840 | S_97_2_14803 | Traction Section Anzac Station section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.814 | S_96_2_14801 | Traction Section Anzac Station | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.771 | S_95_2_14754 | Traction Section State Library to Town hall section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.732 | S_94_2_14751 | Traction Section State Library to Town Hall | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.703 | S_93_2_14703 | Traction Section Parkville to State Library section B | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:40:59.676 | S_92_2_14701 | Traction Section Parkville to State Library | Section Traction Power status Unknown |  |  |  | 0 | SDU | CMS-ESS Interface not connected
CAME UNACK Low | 2024.05.20 11:36:36.736 | DMA-W-PSD-003 | Anzac Platform 1 Zone 1 PSD 03 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:31.515 | DMA-E-PSD-028 | Anzac Platform 2 Zone 3 PSD 28 | PSD isolated |  |  |  | 0 | AZC | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:22.801 | PKV-W-PSD-024 | Parkville Platform 1 Zone 3 PSD 24 | PSD isolated |  |  |  | 0 | PKV | PSD isolated during a blockade
CAME UNACK Low | 2024.05.20 11:36:00.473 | TNC-E-PSD-002 | State Library Platform 2 Zone 1 PSD 02 | PSD isolated |  |  |  | 0 | STL | PSD isolated during a blockade
WENT UNACK Med | 2024.05.28 07:28:32.675 | PKV_ESC_0014 | Escalator 14 Bank 7 (Concourse to Ground Floor) | Escalator stopped(emergency stop button activated!) |  |  | 2024.05.28 07:28:44.669 | 0 | PKV
WENT UNACK Low | 2024.05.28 07:35:16.670 | PKV_ESC_0016 | Escalator 16 Bank 7 (Concourse to Ground Floor) | Escalator failed to start |  |  | 2024.05.28 07:35:28.721 | 0 | PKV
ACK High | 2024.05.20 08:23:30.503 | _Driver2 | MTTHL:_Driver2. | Driver overloaded | 2024.05.20 15:17:54.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.13 17:25:33.702 | _Driver1_2 | MTAZC:_Driver1_2. | Driver overloaded | 2024.05.17 08:14:22.995 | dominic_dlasselle |  | 0 | ARN | Servers Comms
ACK High | 2024.05.10 08:49:20.968 | _Driver2_2 | MTTHL:_Driver2_2. | Driver overloaded | 2024.05.20 15:17:59.449 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK High | 2024.05.08 09:24:26.938 | _Driver1_2 | MTARD:_Driver1_2. | Driver overloaded | 2024.05.20 15:17:40.384 | eric_maddocks |  | 0 | PKV | Servers Comms
ACK Med | 2024.05.20 12:06:59.071 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.068 | _Conn_dist_1_2_to_dist_2_2 | Distributed Server 2 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.066 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.064 | _Conn_dist_1_1_to_dist_2_2 | Distributed Server 1 | Connection lost to Sunshine Server 2 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.062 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.059 | _Conn_dist_1_2_to_dist_2_1 | Distributed Server 2 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.057 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.054 | _Conn_dist_1_1_to_dist_2_1 | Distributed Server 1 | Connection lost to Sunshine Server 1 - Link 0 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Currently not connected to Sunshine
ACK Med | 2024.05.20 12:06:59.001 | _Conn_event_0_2_to_driver_1_2 | Distributed Server 2 | Connection lost | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.20 12:06:58.974 | _Conn_event_0_1_to_driver_1_1 | Distributed Server 1 | Connection lost | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Med | 2024.05.20 12:03:55.572 | _TSC-BMS-PLC_2 | MTTHL:_TSC-BMS-PLC_2. | Communications Fault - Town Hall Server 2 to Town Hall BMS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:55.567 | _TSC-FDS-S7PLUS_2 | MTTHL:_TSC-FDS-S7PLUS_2. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:55.564 | _TSC-FDS-S7PLUS | MTTHL:_TSC-FDS-S7PLUS. | Communications Fault - Town Hall Server 1 to Town Hall FDS PLC | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Med | 2024.05.20 12:03:54.246 | _Mod_Plc_4_2 | MTTHL:_Mod_Plc_4_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2024.05.20 15:18:27.816 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:03:54.234 | _Mod_Plc_3_2 | MTTHL:_Mod_Plc_3_2. | Communications Fault - Town Hall Server 2 to Town Hall EWIS | 2024.05.20 15:18:07.088 | eric_maddocks |  | 0 | AZC
ACK Med | 2024.05.20 12:03:54.231 | _Mod_Plc_2_2 | MTTHL:_Mod_Plc_2_2. | Communications Fault - Town Hall Server 2 to Town Hall FDS Gateway | 2024.05.20 15:18:07.088 | eric_maddocks |  | 0 | AZC | Servers Comms
ACK Med | 2024.05.20 12:03:14.933 | _Mod_Plc_1_2 | Anzac Server 2 | Communications Fault - Anzac Server 2 to Anzac PSD | 2024.05.20 15:18:07.116 | eric_maddocks |  | 0 | ARN
ACK Med | 2024.05.20 12:02:23.399 | _Mod_Plc_1 | Anzac Server 1 | Communications Fault - Anzac Server 1 to Anzac PSD | 2024.05.20 15:18:07.116 | eric_maddocks |  | 0 | AZC
ACK Low | 2024.05.27 14:18:03.648 | PKV_LFT_0009 | Lift 9 BOH (B3 Basement to Ground Floor) | Lift General Fault | 2024.05.27 15:30:50.429 | emilio_ito |  | 0 | PKV | General fault alarm as a result of loss of power
ACK Low | 2024.05.21 09:50:11.517 | AEN_DOR_B1_151-4_1 | Concourse east - back of house emergency corridor | Unauthorised access | 2024.05.21 09:52:39.145 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 12:06:59.010 | _Conn_event_0_2_to_dist_1_2 | Distributed Server 2 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.05.20 12:06:59.006 | _Conn_event_0_1_to_dist_1_1 | Distributed Server 1 | Connection lost - Event to Distribution Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.20 12:06:58.995 | _Conn_event_0_2_to_redu_1_2 | Distributed Server 2 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | THL | Servers Comms
ACK Low | 2024.05.20 12:06:58.990 | _Conn_event_0_1_to_redu_1_1 | Distributed Server 1 | Connection lost - Event to Redundancy Manager - Link 1 | 2024.05.20 15:17:20.301 | eric_maddocks |  | 0 | ARN | Servers Comms
ACK Low | 2024.05.20 11:40:53.209 | AEN_DOR_L2_ESC_STAIRS_5_2 | Level 2 east - back of house stairs | Unauthorised access | 2024.05.21 09:43:32.566 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 11:40:53.176 | AEN_DOR_B2_ESC_STAIRS_04_3 | Platform 1 east - double emergency door | Door open too long | 2024.05.21 09:43:32.566 | harsimran_virk |  | 0 | ARN | Door forced open without using a valid card
ACK Low | 2024.05.20 11:39:46.751 | AEN-SPE-0404 | B1, AEN-SPE-0404, 151-10 BOH Corridor | Heat or smoke detector fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Fire System Currently under Test
ACK Low | 2024.05.20 11:38:16.922 | AEN-FIP-0001 | Arden Main Fire Panel | Fire panels in the station have a fault | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Fire Panel Fault
ACK Low | 2024.05.20 11:37:06.086 | AEN_ESC_0007 | Escalator 7 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.20 11:37:05.402 | AEN_ESC_0006 | Escalator 6 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service
ACK Low | 2024.05.20 11:37:04.724 | AEN_ESC_0005 | Escalator 5 Bank 5 (Concourse to Ground Floor) | Escalator communications lost | 2024.05.21 09:43:32.472 | harsimran_virk |  | 0 | ARN | Escalators out of service